## Inputs
ANARITA BESS — MONTHLY MODEL WITH SCENARIOS
2 × 5 MW / 20 MWh ¦ €4,760,000 ¦ Muminjon (Spanercom)
Yellow cells are modifiable — change to run your own scenarios
PV PARK
Parameter | Value | Unit | Notes
PV Installed Capacity | 10 | MW | Client
Total PV Panels | 15178 |  | 7,586 East + 7,592 West (ASTRO 660Wp)
Panels Removed for BESS | 90 |  | Lost to BESS foundation area
Panel Wattage | 660 | Wp | ASTROENERGY ASTRO 6 CHSM66M-HC
Effective PV Capacity |  | kWp
Annual Specific Yield | 1932 | kWh/kWp | PVSyst verified
Effective Annual Production |  | MWh
PV Revenue Price (solar-hour avg) | 140.88 | EUR/MWh | TSOC DAM 134-day (06:00-17:00)
PV Annual Degradation | 0.5% |  | 0.5%/yr
Annual PV Revenue Loss (panels) |  | EUR/yr | Revenue lost per year from removing 90 panels
BESS SYSTEM
BESS Energy (Total) | 40 | MWh | 2 × 20 MWh (4 × 5 MWh containers per park)
BESS Power | 10 | MW | 2 × 5 MW
BESS EPC Price | 4760000 | EUR | €119/kWh ¦ 2 × €2,380,000
Round-Trip Efficiency (RTE) | 86.32% |  | Linyang AC-AC full system
BESS Availability | 97% |  | 97% guaranteed (LTSA)
LTSA Cost Rate | 2469.59 | EUR/MWh/yr | Confirmed Linyang RFI V3
BESS Insurance | 15000 | EUR/yr | Budget estimate
Annual O&M + Insurance |  | EUR/yr
SCENARIO CONTROL
Curtailment Scenario Multiplier | 1 |  | 1.0 = actual data. Set 1.1 = +10% curtailment across all months. Set 1.3 = +30% etc.
Effective curtailment = Base × Multiplier (capped at 95%)
SOH DATA
Year 0 | 100%
Year 1 | 94.62%
Year 2 | 92.66%
Year 3 | 90.7%
Year 4 | 88.74%
Year 5 | 86.78%
Year 6 | 85.34%
Year 7 | 83.9%
Year 8 | 82.46%
Year 9 | 81.02%
Year 10 | 79.58%
Year 11 | 78.39%
Year 12 | 77.2%
Year 13 | 76.01%
Year 14 | 74.82%
Year 15 | 73.61%

## Monthly Model
MONTHLY BESS REVENUE MODEL — YEAR 1
Based on actual Anarita monthly curtailment profile × scenario multiplier
Month | Days | PVSyst (MWh) | Base Curt % | Eff Curt % | Curtailed (MWh) | Daily Curt (MWh) | BESS Eff (MWh) | Daily Capture | Monthly Cap (MWh) | Dischgd (MWh) | Peak Price | Revenue (€) | O&M (€) | Net (€)
Jan | 31 | 955 | 49% | [7 empty] | 188.26
Feb | 28 | 1086 | 45% | [7 empty] | 191.88
Mar | 31 | 1513 | 66% | [7 empty] | 182.99
Apr | 30 | 1669 | 67% | [7 empty] | 182.99
May | 31 | 1921 | 52% | [7 empty] | 182.99
Jun | 30 | 1987 | 28% | [7 empty] | 182.99
Jul | 31 | 2034 | 27% | [7 empty] | 182.99
Aug | 31 | 1944 | 39% | [7 empty] | 182.99
Sep | 30 | 1724 | 44% | [7 empty] | 182.99
Oct | 31 | 1461 | 59% | [7 empty] | 177.69
Nov | 30 | 1108 | 44% | [7 empty] | 184.77
Dec | 31 | 922 | 27% | [7 empty] | 147.55
TOTAL
YEAR 1 SUMMARY
Gross Revenue
Total O&M
Net BESS Income
Panel Loss Revenue Impact
Net Income After Panel Loss
ROI (after panel loss)
Simple Payback

## Scenarios
SCENARIO COMPARISON — CURTAILMENT MULTIPLIERS
Shows impact of different curtailment levels on returns
Metric | Baseline (1.0×) | Moderate (+20%) | High (+40%) | Very High (+55%)
Weighted Avg Curtailment | 45.26% | 54.31% | 63.36% | 68.74%
Annual Curtailed (MWh) | 8293.09 | 9951.708 | 11610.326 | 12596.134
Annual Captured (MWh) | 8044.2973 | 9404.0026 | 10375.9173 | 10962.8813
Annual Discharged (MWh) | 6943.8374 | 8117.535 | 8956.4918 | 9463.1592
BESS Utilisation | 60.03% | 70.18% | 77.43% | 81.81%
Gross Revenue (EUR) | 1265869.6656 | 1479687.9568 | 1632400.6939 | 1724972.0613
O&M + Insurance | 113783.6 | 113783.6 | 113783.6 | 113783.6
Panel Loss (90 panels) | 16167.5015 | 16167.5015 | 16167.5015 | 16167.5015
Net Income (after panel loss) | 1135918.5641 | 1349736.8553 | 1502449.5924 | 1595020.9598
ROI | 23.86% | 28.36% | 31.56% | 33.51%
Simple Payback (years) | 4.1904 | 3.5266 | 3.1682 | 2.9843
SCENARIO DEFINITIONS
Baseline (1.0×) | Actual 2024-2025 monthly curtailment data as recorded
Moderate (+20%) | Each month's curtailment increased by 20% — reflects near-term trend
High (+40%) | Each month +40% — reflects 1-2 year outlook with more PV online
Very High (+55%) | Each month +55% — reflects 2-3 year outlook, high solar penetration

## 15-Year Projection
15-YEAR PROJECTION (Monthly-Based)
Uses monthly model results for Year 1, then degrades PV and SOH
Year | PV Prod | SOH % | BESS Rev | O&M | Panel Loss | Net Income | Cumulative
1 |  | 94.62%
2 |  | 92.66%
3 |  | 90.7%
4 |  | 88.74%
5 |  | 86.78%
6 |  | 85.34%
7 |  | 83.9%
8 |  | 82.46%
9 |  | 81.02%
10 |  | 79.58%
11 |  | 78.39%
12 |  | 77.2%
13 |  | 76.01%
14 |  | 74.82%
15 |  | 73.61%
SUMMARY
Total Net Income
BESS Investment
Return Multiple
Total Panel Loss (15yr)

## Park Data
ACTUAL PARK DATA — Spanercom Anarita
Month | Yield (MWh) | Potential (MWh) | PVSyst (MWh) | Curtailment %
May-24 | 1023 | 1854 | 1921 | 45%
Jun-24 | 1670 | 1888 | 1987 | 12%
Jul-24 | 1791 | 1916 | 2034 | 7%
Aug-24 | 1703 | 1788 | 1944 | 5%
Sep-24 | 1225 | 1589 | 1724 | 23%
Oct-24 | 941 | 1617 | 1461 | 42%
Nov-24 | 645 | 1160 | 1108 | 44%
Dec-24 | 694 | 951 | 922 | 27%
Jan-25 | 600 | 1179 | 955 | 49%
Feb-25 | 655 | 1198 | 1086 | 45%
Mar-25 | 566 | 1648 | 1513 | 66%
Apr-25 | 578 | 1731 | 1669 | 67%
May-25 | 850 | 1769 | 1921 | 52%
Jun-25 | 1376 | 1898 | 1987 | 28%
Jul-25 | 1438 | 1968 | 2034 | 27%
Aug-25 | 1147 | 1878 | 1944 | 39%
Sep-25 | 965 | 1725 | 1724 | 44%
Oct-25 | 467 | 1139 | 1461 | 59%