## Remote signaling quantity
Note: 1. Address rule for remote signaling quantity: address = base address + telecontrol number 2. The default base address is 1, it can be configured to change.
Telecontrol No. | Address (default) | Address (decimal) | Point Description | Remark | Level (NA/Alarm/Fault)
0 | 0x01 | 1 | Insulation resistance abnormal | 0-Normal 1-Abnormal | Alarm/Fault (configurable)
1 | 0x02 | 2 | AC residual current abnormal | 0-Normal 1-Abnormal | Fault
2 | 0x03 | 3 | DC over-voltage | 0-Normal 1-Abnormal | Fault
3 | 0x04 | 4 | Grid over-voltage abnormal | 0-Normal 1-Abnormal | Fault
4 | 0x05 | 5 | Grid under-voltage abnormal | 0-Normal 1-Abnormal | Fault
5 | 0x06 | 6 | Grid over-frequency abnormal | 0-Normal 1-Abnormal | Fault
6 | 0x07 | 7 | Grid under-frequency abnormal | 0-Normal 1-Abnormal | Fault
7 | 0x08 | 8 | Power module over-temperature | 0-Normal 1-Abnormal | Fault
8 | 0x09 | 9 | Grid phase sequence abnormal | 0-Normal 1-Abnormal | Fault
9 | 0x0A | 10 | Inverter software over-current | 0-Normal 1-Abnormal | Fault
10 | 0x0B | 11 | DC softstart abnormal | 0-Normal 1-Abnormal | Fault
11 | 0x0C | 12 | DC switch abnormal | 0-Normal 1-Abnormal | Fault
12 | 0x0D | 13 | AC fan abnormal | 0-Normal 1-Abnormal | Alarm
13 | 0x0E | 14 | AC switch abnormal | 0-Normal 1-Abnormal | Fault
14 | 0x0F | 15 | Temperature switch abnormal | 0-Normal 1-Abnormal | Fault
15 | 0x10 | 16 | Inner abnormal | 0-Normal 1-Abnormal | Fault
16 | 0x11 | 17 | Inner over-temperature | 0-Normal 1-Abnormal | Fault
17 | 0x12 | 18 | AC softstart abnormal | 0-Normal 1-Abnormal | Fault
18 | 0x13 | 19 | Heat exchanger abnormal | 0-Normal 1-Abnormal | Fault
19 | 0x14 | 20 | AC SPD abnormal | 0-Normal 1-Abnormal | Alarm
20 | 0x15 | 21 | Inner EPO fault | 0-Normal 1-Abnormal | Fault
21 | 0x16 | 22 | External EPO fault | 0-Normal 1-Abnormal | Fault
22 | 0x17 | 23 | Bus voltage mismatch startup condition | 0-Normal 1-Abnormal | Fault
23 | 0x18 | 24 | Bus over-current | 0-Normal 1-Abnormal | Fault
24 | 0x19 | 25 | Zero-offset correction abnormal | 0-Normal 1-Abnormal | Fault
25 | 0x1A | 26 | Access control alarm | 0-Normal 1-Abnormal | Alarm
26 | 0x1B | 27 | Phase lock abnormal | 0-Normal 1-Abnormal | Fault
27 | 0x1C | 28 | DC SPD abnormal | 0-Normal 1-Abnormal | Alarm
28 | 0x1D | 29 | Smart meter communication abnormal | 0-Normal 1-Abnormal | NA
29 | 0x1E | 30 | Inverter hardware over-current | 0-Normal 1-Abnormal | Fault
30 | 0x1F | 31 | Driver abnormal | 0-Normal 1-Abnormal | Fault
31 | 0x20 | 32 | ID conflict | 0-Normal 1-Abnormal | Alarm
32 | 0x21 | 33 | Info sharing CAN communication abnormal | 0-Normal 1-Abnormal | Fault
33 | 0x22 | 34 | Parallel communication wire abnormal | 0-Normal 1-Abnormal | Fault
34 | 0x23 | 35 | Sync CAN communication abnormal | 0-Normal 1-Abnormal | Fault
35 | 0x24 | 36 | DC arc abnormal | 0-Normal 1-Abnormal | Fault
36 | 0x25 | 37 | Zero-sequence over-current | 0-Normal 1-Abnormal | Fault
37 | 0x26 | 38 | DC main contactor abnormal | 0-Normal 1-Abnormal | Fault
38 | 0x27 | 39 | Smog alarm | 0-Normal 1-Abnormal | Alarm
39 | 0x28 | 40 | Parallel communication abnormal | 0-Normal 1-Abnormal | Alarm
40 | 0x29 | 41 | HMI CAN communication abnormal | 0-Normal 1-Abnormal | Alarm
41 | 0x2A | 42 | Model setting error | 0-Normal 1-Abnormal | Fault
42 | 0x2B | 43 | HMI RS485 communication abnormal | 0-Normal 1-Abnormal | Fault
43 | 0x2C | 44 | Remote communication abnormal | 0-Normal 1-Abnormal | Fault
44 | 0x2D | 45 | Fault (total) | 0-Normal 1-Abnormal | Fault
45 | 0x2E | 46 | Alarm (total) | 0-Normal 1-Abnormal | Alarm
46 | 0x2F | 47 | DC parallel model setting error | 0-Normal 1-Abnormal | Fault
47 | 0x30 | 48 | System parameters mismatch | 0-Normal 1-Abnormal | Fault
48 | 0x31 | 49 | Grid voltage unbalance alarm | 0-Normal 1-Abnormal | Alarm
49 | 0x32 | 50 | Low voltage ride through running | 0-Normal 1-Abnormal | Alarm
50 | 0x33 | 51 | High voltage ride through running | 0-Normal 1-Abnormal | Alarm
51 | 0x34 | 52 | DC fan abnormal | 0-Normal 1-Abnormal | Alarm
52 | 0x35 | 53 | Heat sink temperature switch abnormal | 0-Normal 1-Abnormal | Fault
53 | 0x36 | 54 | External temperature switch abnormal | 0-Normal 1-Abnormal | Fault
54 | 0x37 | 55 | Auxiliary power transformer temperature switch abnormal | 0-Normal 1-Abnormal | Fault
55 | 0x38 | 56 | Inductor temperature switch abnormal | 0-Normal 1-Abnormal | Fault
56 | 0x39 | 57 | Positive grounding abnormal | 0-Normal 1-Abnormal | Fault
57 | 0x3A | 58 | Negative grounding abnormal | 0-Normal 1-Abnormal | Fault
58 | 0x3B | 59 | AC grounding abnormal | 0-Normal 1-Abnormal | Fault
59 | 0x3C | 60 | Grid-tied grounding abnormal | 0-Normal 1-Abnormal | Fault
60 | 0x3D | 61 | BMS emergency power off | 0-Normal 1-Abnormal | Fault
61 | 0x3E | 62 | Reserved | 0-Normal 1-Abnormal | NA
62 | 0x3F | 63 | Grid over-frequency/under-frequency standby alarm | 0-Normal 1-Abnormal | Alarm
63 | 0x40 | 64 | Power module over-temperature alarm | 0-Normal 1-Abnormal | Alarm
64 | 0x41 | 65 | Battery over-voltage | 0-Normal 1-Abnormal | Fault
65 | 0x42 | 66 | Battery under-voltage with light-load | 0-Normal 1-Abnormal | Fault
66 | 0x43 | 67 | DC over-current | 0-Normal 1-Abnormal | Fault
67 | 0x44 | 68 | Output voltage abnormal | 0-Normal 1-Abnormal | Fault
68 | 0x45 | 69 | Output voltage mismatch off-grid condition | 0-Normal 1-Abnormal | Fault
69 | 0x46 | 70 | Overload protection | 0-Normal 1-Abnormal | Fault
70 | 0x47 | 71 | Short-circuit protection | 0-Normal 1-Abnormal | Fault
71 | 0x48 | 72 | Inner fan abnormal | 0-Normal 1-Abnormal | Fault
72 | 0x49 | 73 | DC fuse abnormal | 0-Normal 1-Abnormal | Fault
73 | 0x4A | 74 | Battery under-voltage with heavy-load | 0-Normal 1-Abnormal | Fault
74 | 0x4B | 75 | Battery under-voltage alarm | 0-Normal 1-Abnormal | Alarm
75 | 0x4C | 76 | External fan abnormal | 0-Normal 1-Abnormal | Fault
76 | 0x4D | 77 | Battery reverse connected | 0-Normal 1-Abnormal | Fault
77 | 0x4E | 78 | Battery voltage mismatch charge condition | 0-Normal 1-Abnormal | Fault
78 | 0x4F | 79 | Overload alarm | 0-Normal 1-Abnormal | Alarm
79 | 0x50 | 80 | DC arc module communication abnormal | 0-Normal 1-Abnormal | Fault
80 | 0x51 | 81 | BMS system fault | 0-Normal 1-Abnormal | Fault
81 | 0x52 | 82 | BMS communication abnormal | 0-Normal 1-Abnormal | Fault
82 | 0x53 | 83 | BMS dry contact abnormal | 0-Normal 1-Abnormal | Fault
83 | 0x54 | 84 | BMS charge disabled | 0-Normal 1-Abnormal | Alarm
84 | 0x55 | 85 | BMS discharge disabled | 0-Normal 1-Abnormal | Alarm
85 | 0x56 | 86 | BMS standby | 0-Normal 1-Abnormal | Alarm
86 | 0x57 | 87 | BMSAlarm | 0-Normal 1-Abnormal | Alarm
87 | 0x58 | 88 | Reserved | 0-Normal 1-Abnormal | NA
88 | 0x59 | 89 | Heat sink over-temperature alarm | 0-Normal 1-Abnormal | Alarm
89 | 0x5A | 90 | Fault (total) | 0-Normal 1-Abnormal | Fault
90 | 0x5B | 91 | Alarm (total) | 0-Normal 1-Abnormal | Alarm
91 | 0x5C | 92 | AC fan lifespan abnormal | 0-Normal 1-Abnormal | Fault
92 | 0x5D | 93 | DC fan lifespan abnormal | 0-Normal 1-Abnormal | Fault
93 | 0x5E | 94 | AC switch lifespan abnormal | 0-Normal 1-Abnormal | Fault
94 | 0x5F | 95 | DC switch lifespan abnormal | 0-Normal 1-Abnormal | Fault
95 | 0x60 | 96 | Reserved | 0-Normal 1-Abnormal | NA
96 | 0x61 | 97 | Reserved | 0-Normal 1-Abnormal | NA
97 | 0x62 | 98 | Reserved | 0-Normal 1-Abnormal | NA
98 | 0x63 | 99 | Reserved | 0-Normal 1-Abnormal | NA
99 | 0x64 | 100 | Reserved | 0-Normal 1-Abnormal | NA
100 | 0x65 | 101 | Reserved | 0-Normal 1-Abnormal | NA
101 | 0x66 | 102 | Reserved | 0-Normal 1-Abnormal | NA
102 | 0x67 | 103 | Reserved | 0-Normal 1-Abnormal | NA
103 | 0x68 | 104 | Reserved | 0-Normal 1-Abnormal | NA
104 | 0x69 | 105 | Reserved | 0-Normal 1-Abnormal | NA
105 | 0x6A | 106 | Reserved | 0-Normal 1-Abnormal | NA
106 | 0x6B | 107 | Reserved | 0-Normal 1-Abnormal | NA
107 | 0x6C | 108 | Reserved | 0-Normal 1-Abnormal | NA
108 | 0x6D | 109 | Reserved | 0-Normal 1-Abnormal | NA
109 | 0x6E | 110 | Reserved | 0-Normal 1-Abnormal | NA
110 | 0x6F | 111 | Reserved | 0-Normal 1-Abnormal | NA
111 | 0x70 | 112 | Reserved | 0-Normal 1-Abnormal | NA
112 | 0x71 | 113 | ON/OFF status | 0-OFF 1-ON | NA
113 | 0x72 | 114 | PCS normal halt status | 0-Abnormal halt; 1-Normal halt | NA
114 | 0x73 | 115 | PCS standby status | 0-Non standby; 1-Standby | NA
115 | 0x74 | 116 | PCS charge status | 0-Non charge; 1-Charge | NA
116 | 0x75 | 117 | PCS discharge status | 0-Non discharge; 1-Discharge | NA
117 | 0x76 | 118 | PCS fault halt status | 0-Normal; 1-Fault halt | NA
118 | 0x77 | 119 | AC switch status | 0-OFF; 1-ON | NA
119 | 0x78 | 120 | DC switch status | 0-OFF; 1-ON | NA
120 | 0x79 | 121 | PCS Grid-tied status | 0-Non grid-tied; 1-Grid-tied | NA
121 | 0x7A | 122 | PCS off-grid status | 0-Non off-grid; 1-Off-grid | NA
122 | 0x7B | 123 | Remote input/exit status | 0-Exit 1-Input | NA
123 | 0x7C | 124 | Reserved | 0-Normal 1-Abnormal | NA
124 | 0x7D | 125 | Reserved | 0-Normal 1-Abnormal | NA
125 | 0x7E | 126 | Reserved | 0-Normal 1-Abnormal | NA
126 | 0x7F | 127 | Reserved | 0-Normal 1-Abnormal | NA
127 | 0x80 | 128 | Reserved | 0-Normal 1-Abnormal | NA
128-255 |  |  | Reserved | 0-Normal 1-Abnormal | NA

## Telemetering quantity
Note: 1. Address rule for telemetering quantity: address = base address + telecontrol number 2. The default base address is 16385, it can be configured to change. 3. The data is short floating-point type.
Category | Telecontrol No. | Address (default) | Address (decimal) | Point Description | Coefficient | Remark (accuracy, unit)
System telemetering quantity | 0 | 0x4001 | 16385 | Running status | 1 | 0: Halt (no fault and the contactor is disconnected); 1: Standby (no fault and the contactor is closed, and with no charge/discharge power); 2: Fault (with fault, the contactor is disconnected); 3: Charge (stay in charging status); 4: Discharge (stay in discharging status); 5: Charge derating (stay in charging status, derating for over-temperature); 6: Discharge derating (stay in discharging status, derating for over-temperature)
| 1 | 0x4002 | 16386 | Apparent power | 1 | kVA
| 2 | 0x4003 | 16387 | Active power | 1 | kW
| 3 | 0x4004 | 16388 | Reactive power | 1 | kVar
| 4 | 0x4005 | 16389 | Reserved | 1
| 5 | 0x4006 | 16390 | Reserved | 1
| 6 | 0x4007 | 16391 | Power factor | 1
| 7 | 0x4008 | 16392 | Output U current | 1 | A
| 8 | 0x4009 | 16393 | Output V current | 1 | A
| 9 | 0x400A | 16394 | Output W current | 1 | A
| 10 | 0x400B | 16395 | Day charged | 1 | kWh
| 11 | 0x400C | 16396 | Day discharged | 1 | kWh
| 12 | 0x400D | 16397 | Total charged | 1 | kWh
| 13 | 0x400E | 16398 | Total discharged | 1 | kWh
| 14 | 0x400F | 16399 | Grid U/UV voltage | 1 | V
| 15 | 0x4010 | 16400 | Grid V/VW voltage | 1 | V
| 16 | 0x4011 | 16401 | Grid W/WU voltage | 1 | V
| 17 | 0x4012 | 16402 | DC voltage | 1 | V
| 18 | 0x4013 | 16403 | DC current | 1 | A
| 19 | 0x4014 | 16404 | DC power | 1 | kW
| 20 | 0x4015 | 16405 | Frequency | 1 | Hz
| 21 | 0x4016 | 16406 | Inner temperature | 1 | ℃
| 22 | 0x4017 | 16407 | On-grid/off-grid status | 1 | 0-Grid-tied; 1-Off-grid; 2-VSG;3-Grid forming; 4-Auto grid-tied/off-grid
| 23 | 0x4018 | 16408 | Available power | 1 | kVA
| 24 | 0x4019 | 16409 | Total load ratio | 1 | %
| 25 | 0x401A | 16410 | AC residual current | 1 | mA
| 26 | 0x401B | 16411 | Insulation resistance | 1 | kΩ
| 27 | 0x401C | 16412 | AC side total charge active power | 1 | kW
| 28 | 0x401D | 16413 | AC side total charge reactive power | 1 | kVar
| 29 | 0x401E | 16414 | AC side total discharge active power | 1 | kW
| 30 | 0x401F | 16415 | AC side total discharge reactive power | 1 | kVar
| 31 | 0x4020 | 16416 | Max. capacitive reactive power capacity | 1 | 1kVar
| 32 | 0x4021 | 16417 | Max. inductive reactive power capacity | 1 | 1kVar
| 33 | 0x4022 | 16418 | Max. chargeable power | 1 | kW
| 34 | 0x4023 | 16419 | Max. dischargeable power | 1 | kW
| 35 | 0x4024 | 16420 | Running status 2 | 1 | 1: Halt 2: Standby 3: Charge 4: Discharge 5: Fault
| 36 | 0x4025 | 16421 | DC side charging current | 1 | A
| 37 | 0x4026 | 16422 | DC side discharging current | 1 | A
| 38 | 0x4027 | 16423 | DC side charging power | 1 | kW
| 39 | 0x4028 | 16424 | DC side discharge power | 1 | kW
| 40 | 0x4029 | 16425 | AC side charging U current | 1 | A
| 41 | 0x402A | 16426 | AC side charging V current | 1 | A
| 42 | 0x402B | 16427 | AC side charging W current | 1 | A
| 43 | 0x402C | 16428 | AC side discharging U current | 1 | A
| 44 | 0x402D | 16429 | AC side discharging V current | 1 | A
| 45 | 0x402E | 16430 | AC side discharging W current | 1 | A
| 46 | 0x402F | 16431 | Reserved | 1
| 47 | 0x4030 | 16432 | Reserved | 1
| 48 | 0x4031 | 16433 | Reserved | 1
| 49 | 0x4032 | 16434 | Reserved | 1
| 50 | 0x4033 | 16435 | BMS system status | 1 | 0: Initial 1: Normal 2: Charge disabled 3: Discharge disabled 4: Alarm 5: Fault 6: Standby
| 51 | 0x4034 | 16436 | Battery pack total voltage | 1 | V
| 52 | 0x4035 | 16437 | Battery pack total current | 1 | A
| 53 | 0x4036 | 16438 | Battery pack SOC | 1 | %
| 54 | 0x4037 | 16439 | Battery pack SOH | 1 | %
| 55 | 0x4038 | 16440 | Charge limited current | 1 | A
| 56 | 0x4039 | 16441 | Discharge limited current | 1 | A
| 57 | 0x403A | 16442 | Charge limited voltage | 1 | V
| 58 | 0x403B | 16443 | Discharge limited voltage | 1 | V
| 59 | 0x403C | 16444 | Available charged energy | 1 | kWh
| 60 | 0x403D | 16445 | Available discharged energy | 1 | kWh
| 61 | 0x403E | 16446 | Reserved | 1
| 62 | 0x403F | 16447 | Reserved | 1
| 63 | 0x4040 | 16448 | Reserved | 1
| 64 | 0x4041 | 16449 | Reserved | 1
| 65 | 0x4042 | 16450 | Reserved | 1
| 66 | 0x4043 | 16451 | Reserved | 1
| 67 | 0x4044 | 16452 | Reserved | 1
| 68 | 0x4045 | 16453 | Reserved | 1
| 69 | 0x4046 | 16454 | Reserved | 1
| 70 | 0x4047 | 16455 | Reserved | 1
| 71-254 | 0x4048~0X40FF
Return value of teleadjusting | 255 | 0x4100 | 16640 | Return value of teleadjusting_Auto-start when power on | 1 | 0-Disable; 1-Enable
| 256 | 0x4101 | 16641 | Return value of teleadjusting_On-grid/off-grid mode | 1 | 0-Grid-tied; 1-Off-grid; 2-VSG;3-Grid forming; 4-Auto grid-tied/off-grid
| 257 | 0x4102 | 16642 | Return value of teleadjusting_H/LVRT | 1 | 0-Disable; 1-Enable(Reactive Support Mode);2-Enable(Zero Current Mode);
| 258 | 0x4103 | 16643 | Return value of teleadjusting_Active islanding | 1 | 0-Disable; 1-Enable
| 259 | 0x4104 | 16644 | Return value of teleadjusting_System running mode | 1 | 0-Constant power; 1-Constant current
| 260 | 0x4105 | 16645 | Return value of teleadjusting_Reactive power running mode | 1 | 0-Constant reactive power; 1-Constant power factor
| 261 | 0x4106 | 16646 | Return value of teleadjusting_Active power | 1 | Accuracy: 1kW
| 262 | 0x4107 | 16647 | Return value of teleadjusting_Reactive power | 1 | Accuracy: 1kVar
| 263 | 0x4108 | 16648 | Return value of teleadjusting_Power factor | 1 | Accuracy: 0.01
| 264 | 0x4109 | 16649 | Return value of teleadjusting_Discharge locked time | 1 | Accuracy: 1s
| 265 | 0x410A | 16650 | Return value of teleadjusting_Power prestart rate | 1 | Accuracy: 0.01%/s (it is the power change rate during operating)
| 266 | 0x410B | 16651 | Return value of teleadjusting_Current of constant current mode | 1 | Accuracy: 0.1A (It is valid when the running mode is constant current. +: battery discharge, -:battery charge)
| 267 | 0x410C | 16652 | Return value of teleadjusting_DC voltage of constant voltage mode | 1 | Accuracy: 0.1V
| 268 | 0x410D | 16653 | Return value of teleadjusting_Reserved | 1
| 269 | 0x410E | 16654 | Return value of teleadjusting_Reserved | 1
| 270 | 0x410F | 16655 | Return value of teleadjusting_Reserved | 1
| 271 | 0x4110 | 16656 | Return value of teleadjusting_Reserved | 1
| 272 | 0x4111 | 16657 | Return value of teleadjusting_Reserved | 1
| 273 | 0x4112 | 16658 | Return value of teleadjusting_Reserved | 1
| 274 | 0x4113 | 16659 | Return value of teleadjusting_Reserved | 1
| 275 | 0x4114 | 16660 | Return value of teleadjusting_Reserved | 1
| 276 | 0x4115 | 16661 | Return value of teleadjusting_Reserved | 1
| 277 | 0x4116 | 16662 | Return value of teleadjusting_Reserved | 1
| 278 | 0x4117 | 16663 | Return value of teleadjusting_Reserved | 1
| 279 | 0x4118 | 16664 | Return value of teleadjusting_Reserved | 1
| 280 | 0x4119 | 16665 | Return value of teleadjusting_Reserved | 1
| 281 | 0x411A | 16666 | Return value of teleadjusting_Reserved | 1
| 282 | 0x411B | 16667 | Return value of teleadjusting_Reserved | 1
| 283 | 0x411C | 16668 | Return value of teleadjusting_Reserved | 1
| 284 | 0x411D | 16669 | Return value of teleadjusting_Reserved | 1
| 285~511 | 0x411E~0x4200 |  | Reserved | 1

## Remote control quantity
Note: 1. Address rule for remote control quantity: address = base address + telecontrol number 2. The default base address is 24577, it can be configured to change.
Category | Telecontrol No. | Address (default) | Address (decimal) | Point Description | Remark (unit)
System parameter | 0 | 0x6001 | 24577 | ON/OFF | 0-OFF; 1-ON
| 1~10 | 0x6002~0x600A | 24578~24586 | Reserved | Reserved

## Teleadjusting quantity
Note: 1. Address rule for teleadjusting quantity: address = base address + telecontrol number 2. The default base address is 25089, it can be configured to change. 3. The data is short floating-point type.
Category | Telecontrol No. | Address (default) | Address (decimal) | Point Description | Remark
Ssystem parameter | 0 | 0x6201 | 25089 | Auto-start when power on | 0-Disable; 1-Enable
| 1 | 0x6202 | 25090 | On-grid/off-grid mode | 0-Grid-tied; 1-Off-grid; 2-VSG;3-Grid forming; 4-Auto grid-tied/off-grid
| 2 | 0x6203 | 25091 | H/LVRT | 0-Disable; 1-Enable(Reactive Support Mode);2-Enable(Zero Current Mode);
| 3 | 0x6204 | 25092 | Active islanding | 0-Disable; 1-Enable
| 4 | 0x6205 | 25093 | System running mode | 0-Constant power; 1-Constant current
| 5 | 0x6206 | 25094 | Reactive power running mode | 0-Constant reactive power; 1-Constant power factor
| 6 | 0x6207 | 25095 | Active power setting | Accuracy: 1kW
| 7 | 0x6208 | 25096 | Reactive power setting | Accuracy: 1kVar
| 8 | 0x6209 | 25097 | Power factor setting | Accuracy: 0.01
| 9 | 0x620A | 25098 | Discharge locked time | Accuracy: 1s
| 10 | 0x620B | 25099 | Power prestart rate | Accuracy: 0.01%/s, it is the power change rate during operating.
| 11 | 0x620C | 25100 | Current of constant current mode | Accuracy: 0.1A (It is valid when the running mode is constant current. +: battery discharge, -:battery charge)
| 12 | 0x620D | 25101 | DC voltage of constant voltage mode | Accuracy: 0.1V
| 13 | 0x620E | 25102 | Reserved
| 14 | 0x620F | 25103 | Reserved
| 15 | 0x6210 | 25104 | Reserved
| 16 | 0x6211 | 25105 | Reserved
| 17 | 0x6212 | 25106 | Reserved
| 18 | 0x6213 | 25107 | Reserved
| 19 | 0x6214 | 25108 | Reserved
| 20 | 0x6215 | 25109 | Reserved
| 21 | 0x6216 | 25110 | Reserved
| 22 | 0x6217 | 25111 | Reserved
| 23 | 0x6218 | 25112 | Reserved
| 24 | 0x6219 | 25113 | Reserved
| 25 | 0x621A | 25114 | Reserved
| 26 | 0x621B | 25115 | Reserved
| 27 | 0x621C | 25116 | Reserved
| 28 | 0x621D | 25117 | Reserved
| 29 | 0x621E | 25118 | Reserved