OPERATIONAL PLAN | LTSA LCY-LTSA-GAL-2026

OPERATIONS AND MAINTENANCE PLAN (O&M)

BESS SYSTEM - GALASCOPE 1 AND GALASCOPE 2

Implementation document for Tier C services: 24/7 monitoring, preventive and corrective maintenance, incident response, availability guarantee and preservation of OEM warranty rights.

| Field | Value | Field | Value |
| --- | --- | --- | --- |
| Project | Galascope 1 / Galascope 2 | Status | REV.3 - DRAFT FOR REVIEW |
| BESS Capacity | 20 MWh + 10 MWh = 30 MWh | BESS AC Power | 5.0 MW + 2.5 MW = 7.5 MW |
| Technology | Linyang Power Atlantic 5 MWh, LFP | EMS/SCADA | DISPERON |
| Service Level | Tier C (default from PAC) | O&M Contractor | Lighthief Cyprus Ltd |
| Client | Galascope Ltd | Document Type | Plan O&M |
| Base Document | LTSA v4.7 / Annex LT-2 | Governing LTSA Language | English |

DOCUMENT STATUS: Working version following investor review. The Plan becomes a controlled document once the pre-PAC conditions have been closed, the duty roster has been approved and the Parties have signed it. The final controlled version for the Client shall be issued in English. In the event of conflict, the LTSA shall prevail and, within the LTSA, Annex LT-2 shall prevail.

Document Control Table

| Revision | Change Description | Prepared by | Approved by |
| --- | --- | --- | --- |
| Rev.0 | Initial project plan based on LTSA v4.7 and the Lighthief draft | Lighthief | [TO BE COMPLETED] |
| Rev.1 | EOA data, BESS capacities, locations, permits, site obligations and named list of responsible persons | Lighthief | [TO BE COMPLETED] |
| Rev.2 | Investor review: SLA, PAC conditions, availability, spares, SOH/RTE and stop-clock | Lighthief | [TO BE COMPLETED] |
| Rev.3 | GPS coordinates (Galascope 1 & 2) and PCS/Transformer/MVS technical data completed from SA-13/SA-14; RMU brand confirmed Mingyang (Linyang/Costas, Aug 2026) [13 Aug 2026: corrected LTSA version citation from v6.5 to v4.3] [14 Aug 2026: LTSA further revised to v4.6 (Annex LT-2 fully integrated inline) — citation updated accordingly.] [18 Aug 2026: LTSA further revised to v4.7 (fixed Schedule/Annex-V6 drafting artifacts) — citation updated accordingly.] | Lighthief | [TO BE COMPLETED] |

Contents and Document Map

| Section | Scope |
| --- | --- |
| 1 | Status, Purpose, Basis and Document Hierarchy |
| 2 | Project Data and System Boundaries |
| 3 | Tier C Service Scope and Exclusions |
| 4 | Responsible Persons, RACI and Communication |
| 5 | Pre-PAC Mobilisation and Operational Readiness |
| 6 | 24/7 Monitoring, SCADA/EMS and Operational Control |
| 7 | Alarms, SLA, Escalation and Incident Management |
| 8 | Preventive Maintenance Programme |
| 9 | Corrective Maintenance and Work Control |
| 10 | HSE, Fire Safety, Environment and Emergency Response |
| 11 | Spare Parts, Warehouse and Obsolescence |
| 12 | Availability, SOH, RTE and Warranty Management |
| 13 | Reporting, Data and Cybersecurity |
| 14 | Regulatory Compliance, DSO and Competence |
| 15 | Quality, Audits and Improvement |
| 16 | Service Completion and Handover |
| A-D | Schedules, checklists, matrices and source registers |

1.  STATUS, PURPOSE, BASIS AND DOCUMENT HIERARCHY

1.1 Purpose of the Plan

This O&M Plan translates the LTSA provisions into a practical operating system for the two BESS Parks, covering monitoring, on-call organisation, maintenance planning, alarm response, work records, warranty management, spare parts and regulatory compliance. It applies to Lighthief personnel, subcontractors and all persons performing activities within the O&M system boundaries.

1.2 Document Basis and Order of Precedence

LTSA LCY-LTSA-GAL-2026, version v4.7, together with Schedules 1-5.

Annex LT-2 - Agreed Technical & Service Amendments; where it conflicts with the main body, Annex LT-2 shall prevail.

EPC Agreement LCY-EPC-GAL-B1-2026, OEM Direct Warranty Undertaking, OEM Warranty Terms, Technical Agreements, EMS Subscription Agreement and the approved Linyang OEM instructions.

EOA Submission Documents package dated 07.08.2026: designer declarations, BESS site plans dated April 2026, approval certificates, building permits and conditions, CERA/RAEK exemptions, lease agreements, title deeds, cadastral plans and powers of attorney for plots 71/73 and 471/520.

Current site procedures: Emergency Response Plan, LOTO, permits to work, fire protection plan, cybersecurity procedures and DSO/EAC requirements.

CONTROL PRINCIPLE: Any change to OEM instructions, BMS/PCS/EMS/SCADA configuration, DSO requirements or warranty conditions triggers a review of this Plan and the relevant checklists. No activity outside the OEM instructions may be performed without prior OEM authorisation.

1.3 Controlled Status and Reviews

| Event | Required Action |
| --- | --- |
| Before PAC | Complete all open fields, the asset register, contacts, spare-parts list and HSE documents. |
| At least annually | Review of the Plan by the O&M Manager, discipline leads and the Client representative. |
| After a major incident | Update following RCA, closure of corrective actions and approval of changes by the Parties. |
| After a technical/regulatory change | Assess the impact on warranty, safety, SCADA, DSO and the PM schedule. |
| After a permit/site-layout change | Update the Permit Register, site plan, roads, drainage, fencing, security measures and environmental obligations. |
| After a contractual change | Issue a new revision with a change log and formal approval. |

1.4 Operational Definitions

| Term | Operational Meaning |
| --- | --- |
| PAC | Provisional Acceptance Certificate; commencement of Tier C service for the relevant Park. |
| Park | Galascope 1: 5.0 MW / 20 MWh BESS adjacent to a 5.0 MWp PV plant, plots 71/73; Galascope 2: 2.5 MW / 10 MWh BESS adjacent to a 2.5 MWp PV plant, plots 471/520. |
| EOA | District Local Government Organisation of Famagusta - the competent building/local authority for the documentation covered by this Plan. |
| CERA / RAEK | Cyprus Energy Regulatory Authority / Ρυθμιστική Αρχή Ενέργειας Κύπρου. |
| Restoration Time | Time from detection to restoration of safe operating capability, including partial capability. |
| Resolution Time | Time from detection to permanent repair/replacement, recommissioning and incident closure. |
| Critical / Major / Minor Alert | Alarm class determined by the impact on safety, availability, performance and warranty. |
| SOH / SOC / RTE | Battery state of health / state of charge / round-trip efficiency. |
| Unavailable Hours | Time during which the BESS cannot operate at rated power for reasons included under the LTSA. |
| Warranty-Preservation File | A complete, auditable set of warranty-preservation evidence for each Park. |

2.  PROJECT DATA AND SYSTEM BOUNDARIES

2.1 Baseline Configuration

| Item | Galascope 1 | Galascope 2 | Remarks |
| --- | --- | --- | --- |
| Capacity | 20 MWh | 10 MWh | Total 30 MWh |
| Reference PV Plant | 5.0 MWp | 2.5 MWp | Confirmed in CERA/RAEK exemptions E2674/2020 and E2673/2020 |
| BESS AC Power | 5.0 MW | 2.5 MW | In accordance with the 5 MW and 2.5 MW project designations in the EOA package; confirm PCS ratings in the as-built documentation |
| Location | Foinitzi, Avgorou, Famagusta 35°03'53.8"N 33°51'30.0"E | Kerimis, Avgorou, Famagusta 35°03'52.0"N 33°51'47.9"E | GPS per site coordinates provided Aug 2026. Distance to nearest coastline (Famagusta Bay, NE, straight-line — not surveyed): Galascope 1 ≈ 10.0 km, Galascope 2 ≈ 9.7 km. |
| Plots / plan / section | 71 and 73 / 2-278-381 and 2-278- 382 / 12 | 471 and 520 / 2-278-381 / 03 | In accordance with title deeds, powers of attorney and EOA certificates |
| Plot Area | 60,093 m² + 59,159 m² | 13,500 m² + 26,775 m² | Registered plot areas; these do not represent the entire area occupied by the BESS |
| Battery Containers | 4 × Linyang Power Atlantic 5 MWh | 2 × Linyang Power Atlantic 5 MWh | Configuration derived from 20/10 MWh; tags and serial numbers from the asset register |
| Chemistry / Parameters | LFP, 5,015 kWh/container | LFP, 5,015 kWh/container | 12P416S; 45 kW liquid cooling |
| PCS / Transformer / MVS | 4× Kehua PCS BCS1250K-C-HUD (skid: BCS5000K-C-HUD/T4), 5,000 kW 1× step-up transformer 5,000 kVA 22/0.69 kV, oil-immersed, Dy11 1× auxiliary transformer 250 kVA 0.69/0.38 kV, dry-type, Dyn11 1× RMU: Mingyang, 24 kV, SF6-free, 630 A | 2× Kehua PCS BCS1250K-C-HUD (skid: BCS2500K-C-HUD/T2), 2,500 kW 1× step-up transformer 2,500 kVA 22/0.69 kV, oil-immersed, Dy11 1× auxiliary transformer 125 kVA 0.69/0.38 kV, dry-type, Dyn11 1× RMU: Mingyang, 24 kV, SF6-free, 630 A | Per SA-13/SA-14 Technical Agreements v6.5 and OEM.rmu in portfolio-data.ts. RMU brand confirmed Mingyang (Aug 2026, Linyang/Costas). Serial numbers from FAT reports/asset register. |
| EMS/SCADA | DISPERON | DISPERON | Local and global access, DSO interface |
| CERA/RAEK Exemption for PV | E2674/2020; 14.04.2020- 13.04.2050 | E2673/2020; 14.04.2020- 13.04.2050 | Modification/expansion of the plant requires the applicable regulatory procedure |
| PAC / Warranty Start | [TO BE COMPLETED] | [TO BE COMPLETED] | Separately for each Park |

2.2 Locations and Site Infrastructure

| Element | Galascope 1 - plots 71/73 | Galascope 2 - plots 471/520 |
| --- | --- | --- |
| Access | Old Larnaca-Famagusta road; 4 m and 6 m entrance gates; internal roads and unpaved sections. | Public and internal road; 4 m gates; designated parking and access to the EAC room. |
| Fencing / Security | 2.10 m fencing, CCTV, lighting and laser-barrier points. | 2.10 m fencing, CCTV, lighting, laser barriers and lightning- protection points. |
| Water / Drainage | Registered stream No. 303 between the plots; 4 m × 0.30 m channels and cable trenches - no interference with the stream. | Maintain effective stormwater drainage and protect the road reserve and access to EAC infrastructure. |
| Surroundings | Agricultural Zone G2; approximately 2 km from Vrysoulles | Kerimis location in Avgorou; control public access at the site |
|  | and approximately 200 m from the Monastery of Agios Kendeas. | boundary. |
| BESS Plans | Plots 71/73 plan, April 2026; C35 foundations, B420C reinforcing steel. | Plots 471/520 plan, April 2026; C35 foundations, B420C reinforcing steel. |

BESS EOA STATUS: The package contains designer declarations and BESS plans dated April 2026 prepared for the Special Exemption Order 2026 procedure, but it does not contain final confirmation of EOA acceptance/approval for the BESS scope. Before work starts and before PAC, this item shall be closed in the Permit Register and an approved set of stamped drawings/as-built documentation shall be obtained.

2.3 Technical Boundaries and Interface Responsibility

The O&M scope covers the BESS, BMS, PCS, MV/MVS switchgear, transformers within the contractual scope, auxiliary systems, HVAC/liquid cooling, fire detection and suppression systems, SCADA gateway, EMS, DSO telemetry and all interconnections and control functions between these systems. Lighthief is responsible for end-to-end BMS-PCS-SCADA-EMS compatibility, communications, command execution and data integrity throughout the service period. Failure of an affiliate, DISPERON or a subcontractor does not release Lighthief from this responsibility towards the Client.

EXTERNAL BOUNDARY: Grid issues beyond the point of connection, unagreed civil works and third-party equipment may be excluded from the calculation only to the extent that they directly caused the relevant consequences. Monitoring, diagnosis, safe disconnection, impact mitigation, documentation and warranty-claim support remain required.

2.4 Asset and Configuration Register

Asset register per Park: tag, manufacturer, model, serial number, firmware version, warranty date, location and spare part reference.

Single-line electrical diagram, communication architecture, point list, Modbus / IEC 61850 / IEC 60870-5- 104 maps and approved protection settings.

List of user accounts, permissions and remote access rights, including the owner of each account and the review date.

Post-PAC baseline: SOC/SOH, usable AC capacity, RTE, thermal condition, cell imbalance, alarms, software versions and C5 coating condition.

3.  TIER C SERVICE SCOPE AND EXCLUSIONS

3.1 Services Covered by the Plan

| Area | Execution Scope |
| --- | --- |
| Monitoring 24/7/365 | Data collection, alarming, classification, initial diagnosis, notifications and technical on-call duty. |
| Preventive Maintenance | Monthly remote checks, quarterly on-site visits, quarterly health checks and semi-annual and annual tests. |
| Corrective Maintenance | Diagnosis, labour, travel within Cyprus, dismantling/reassembly, configuration restoration, testing and documentation. |
| PCS and MVS | Service and fault handling for the Tier B scope included in Tier C. |
| Emergency Response | Priority response times, isolation, dispatch, restoration and incident reporting. |
| Availability | 97% annual group-level guarantee for G1+G2, with each Park tracked in parallel. |
| Spare Parts | Local stock of critical components in Cyprus, with replenishment and storage-condition control. |
| OEM Warranty | Preservation of warranty conditions, evidence files, claims management and annual performance tests. |
| Reports and Data | Monthly, quarterly and annual reports, raw-data export, incident registers and availability calculations. |
| Compliance | DSO/EAC testing, fire safety, environment, cybersecurity and audit documentation. |
| Site Infrastructure | Routine inspection of access roads, gates, fencing, fauna passages, drainage, the stream, security systems and housekeeping; non-routine civil repairs require a separate order. |

3.2 Exclusions and Classification Rules

Customisation and non-standard expansion of the EMS beyond the standard configuration.

Third-party equipment outside the EPC scope and grid issues beyond the point of connection.

Damage directly caused by Force Majeure, the Client, vandalism or an unauthorised modification.

Civil, structural and site infrastructure works beyond routine maintenance.

Replacement of major components outside warranty/SOH coverage - subject to separate quotation. Each exclusion must be supported by causal evidence identifying the event, extent of impact, period, technical evidence and classification rationale. The Client may reasonably challenge the classification. An exclusion does not limit the duty to take immediate protective action and minimise damage.

4.  RESPONSIBLE PERSONS, RACI AND COMMUNICATION

4.1 Named List of Responsible Persons

| Person | Role | Responsibility under the O&M Plan |
| --- | --- | --- |
| Marcin Niedośpiał | O&M Site Manager | Overall service delivery, Client interface, operational safety, escalations, PM schedule, permit/lease register and report approval. |
| Taras Rybak | Remote Monitoring Manager | Organisation of 24/7 monitoring, duty rosters, alarms, KPIs, platform continuity and shift escalations. |
| Mateusz Kasprzyk | SCADA System Operator | Continuous monitoring, alarm acknowledgement, authorised commands, shift log, telemetry quality and local dispatch. |
| Andrzej Lechowicz | EMS Engineer | EMS logic, BMS-PCS-SCADA-DSO integration, operating schedules, command diagnostics and configuration change control. |
| Wojciech Czyż | O&M Electrical Manager | Electrical supervision, MV/LV, LOTO/PTW, protection, measurements, thermography, DSO/EAC and acceptance of electrical work. |
| Kacper Góral | Electrician | Field work, PM/CM, measurements, connection inspections, fault rectification and work records. |
| Maciej Lachowski | HVAC Manager | Liquid cooling/HVAC, thermal performance, filters, fans, alarms and the auxiliary-equipment repair plan. |
| Zbigniew Janik | Mechanical Engineer | Containers, locks, seals, fixings, corrosion, mechanical components and support for heavy replacements. |
| Mateusz Kozieł | Civil Engineer | Foundations, roads, drainage, the stream, fencing, fauna passages and site- layout compliance with EOA plans. |
| Dimos | External Electrical Designer | Design support, settings and technical/DSO coordination within the formally commissioned scope. |

The table above identifies responsible persons and does not constitute the full shift roster. Telephone numbers, e-mail addresses, deputies, emergency numbers and availability periods shall be finalised in the controlled contact and duty roster before PAC. Official reports and notices to the Client shall be issued in English unless the Parties agree otherwise in writing; English remains the governing language of the LTSA.

4.2 Key Responsibilities

| Area | Responsible Persons | Scope |
| --- | --- | --- |
| Management and HSE | Marcin Niedośpiał | Single point of contact, operational decisions, escalations, emergency plan, HSE coordination and action closure. |
| Monitoring / SCADA / EMS | Taras Rybak, Mateusz Kasprzyk, Andrzej Lechowicz | 24/7 alarms, safe control, data integrity, EMS/SCADA and shift handover. |
| Electrical | Wojciech Czyż, Kacper Góral, Dimos | MV/LV, PTW/LOTO, protection, measurements, DSO, works and post-repair testing. |
| HVAC / Mechanical | Maciej Lachowski, Zbigniew Janik | Thermal performance, cooling, containers and mechanical components. |
| Site / Civil / EOA | Mateusz Kozieł | Foundations, drainage, roads, fencing, the stream and site compliance with permit conditions. |
| Client | Person appointed by Galascope Ltd | Safe access, site documents, internet connectivity, compliant operation, no unauthorised modifications and required insurance. |

4.3 RACI Matrix

| Process | A | R | C | I |
| --- | --- | --- | --- | --- |
| Monitoring and Alarm Classification | Taras Rybak | Mateusz Kasprzyk | Andrzej Lechowicz / Marcin Niedośpiał | Client |
| PM Plan and Visits | Marcin Niedośpiał | Relevant Discipline Leads | OEM | Client |
| Critical Incident | Marcin Niedośpiał | Mateusz Kasprzyk + relevant lead | OEM / DSO / emergency services | Client / Lender's IE |
| Warranty Claim | Marcin Niedośpiał | Relevant Technical Lead | OEM / Client | Lender IE |
| Monthly Report | Marcin Niedośpiał | Taras Rybak / Mateusz Kasprzyk | Discipline Leads | Client |
| EMS/SCADA/Settings Change | Marcin Niedośpiał | Andrzej Lechowicz / Mateusz Kasprzyk | Wojciech Czyż / Dimos / DSO / OEM | Client |
| Site / EOA Compliance | Marcin Niedośpiał | Mateusz Kozieł | Wojciech Czyż / designer | Client |
| Spare-Parts Warehouse | Marcin Niedośpiał | Relevant Technical Lead | OEM | Client |

A - Accountable, R - Responsible, C - Consulted, I - Informed.

5.  PRE-PAC MOBILISATION AND OPERATIONAL READINESS

O&M readiness is a condition for the safe takeover of each Park. Each Park shall pass a separate readiness gate. An open item blocks takeover unless the Client accepts in writing an interim plan identifying the owner, deadline and risk controls.

| Gate | Acceptance Criterion | Owner | Status |
| --- | --- | --- | --- |
| EOA / Permits | Final acceptance of the BESS scope, stamped drawings, authority conditions and no unresolved deviations. | O&M Manager | [ ] |
| As-Built Documentation | GPS, SLD, communication diagrams, datasheets, instructions, settings, certificates and FAT/SAT/PAC protocols. | O&M Manager | [ ] |
| Asset register | Complete asset list, serial numbers, firmware, warranties, locations and photographs. | Back Office | [ ] |
| Monitoring | SCADA/EMS/BMS/PCS online, time synchronisation, point-to-point testing, alarms, redundant channels and notification test. | SCADA | [ ] |
| Cybersecurity | MFA, RBAC, named accounts, VPN, logs, configuration backups and emergency-access procedure. | SCADA / IT | [ ] |
| HSE / ERP | Site-specific ERP, LOTO, PTW, PPE, SDS, 6 m fire-access roads, isolation maps and an emergency-services drill. | HSE | [ ] |
| Local Team | Duty roster, deputies, Cypriot qualifications, Linyang training, EMS/SCADA and fire-safety training. | O&M Manager | [ ] |
| Spare-Parts Warehouse | Signed min/max list, part numbers, ownership, compatibility, storage, replenishment and evidence of availability. | Back Office | [ ] |
| PCS / Transformer | Approved major-component failure strategy: stock, OEM pool, replacement unit or binding lead time. | O&M Manager | [ ] |
| Baseline | 98.5% SOH at COD (LTSA reference), AC capacity, RTE, thermal performance, cell imbalance and C5 condition. | OEM / O&M | [ ] |
| SOH/RTE Protocol | Signed protocol: AC measurement point, auxiliary energy, temperature, C-rate, rest | OEM / O&M | [ ] |
|  | period, data and validity criteria. |  |  |
| External Contacts | Client, DSO/EAC, Fire Service, security, OEM, DISPERON, transport and crane provider. | O&M Manager | [ ] |
| Warranty File | Folder structure, report templates, required photographs/measurements and 15+5-year retention method. | Back Office | [ ] |

PRE-PAC CLOSURE CONDITIONS: Closure evidence is the document identified in the controlled PAC Readiness Register and accepted by the relevant owner and the Client. Absence of evidence means the item remains open. The critical-spares list, SOH/RTE protocol, final EOA/as-built documents, ERP readiness and PCS/transformer strategy shall be closed before PAC or covered by a written, accepted interim plan.

6.  24/7 MONITORING, SCADA/EMS AND OPERATIONAL CONTROL

6.1 Monitored Parameters

| Group | Minimum Scope |
| --- | --- |
| Battery | Cell voltage and temperature; string and container SOC/SOH; current; power limits; cell imbalance; BMS alarms. |
| PCS / MVS / Transformer | Status, trips, P/Q, efficiency, voltage, current, temperature, protection and availability. |
| Thermal Systems | HVAC/liquid cooling, temperatures, flow/status, filters, fans and alarms. |
| Safety | Fire and gas detection, suppression readiness, E-stop, door interlock and auxiliary power. |
| Communications | BMS-PCS-EMS-SCADA, gateway, internet, time synchronisation, data loss and telemetry quality. |
| EMS / Dispatch | Command execution, power limits, schedules, zero-export (if applicable) and integration errors. |
| DSO / EAC | P, Q, V, I, f, SOC, SOH, remote commands, IEC 60870-5-104, PQDIF and COMTRADE. |
| Environment / Cybersecurity | Ambient temperature, humidity, access events, configuration changes and firmware integrity. |

6.2 Monitoring Centre Operating Routine

Continuous monitoring of dashboards and the alarm queue; each alarm shall have a source timestamp.

Acknowledge and classify in accordance with Section 7; failure to acknowledge triggers automatic escalation.

Remote response shall be performed only by authorised persons and in accordance with the approved procedure.

The shift log shall include active alarms, power limitations, open work orders, spare-part status and required follow-up actions.

Shift handover requires acknowledgement by the incoming person; Critical and Major alarms shall also be handed over verbally.

A monitoring platform failure is a Major Alert and becomes a Critical Alert if it affects safety.

6.3 Warranty Protection Thresholds

| Parameter / Condition | Operating Threshold | Action |
| --- | --- | --- |
| Cell Voltage - Pre-Alarm | < 2.9 V | Automatic alarm; immediate trend assessment and safe recharge plan. |
| Cell Voltage - Warranty Void | < 2.8 V for 120 h | Prevent occurrence; Critical escalation and SOC restoration plan. |
| Under-Voltage - Warranty Void | ≤ 2.5 V, any occurrence | Immediate isolation/protection, OEM notification and incident report. |
| SOC During Standstill | > 5% | Maintain above the threshold; low-SOC alarm. |
| Long-Term Standstill | 30-50% SOC | Set before a long shutdown in accordance with OEM instructions. |
| Charging Temperature | 0 to +55°C | Pre-alarm 5°C from the limit; derate/stop in accordance with BMS/OEM. |
| Discharging Temperature | -20 to +55°C | Pre-alarm 5°C from the limit; derate/stop in accordance with BMS/OEM. |
| Humidity | > 90% RH alarm; max. 95% RH | Check sealing, condensation and HVAC; do not open in adverse weather. |

6.4 Command and Configuration Change Control

Start/stop, P-set, Q-set and zero-export commands shall be positively confirmed and recorded in the log.

Any change to protection settings requires designer/DSO approval and a four-eyes check.

Firmware/software updates require OEM authorisation, a backup, rollback plan, service window and functional test.

Every change shall be entered in the configuration register, identifying who, when, reason, version before/after, test result and approval.

Remote control functionality and telemetry completeness shall be tested monthly.

7.  ALARMS, SLA, ESCALATION AND INCIDENT MANAGEMENT

7.1 Alarm Classification

| Class | Criterion | Examples |
| --- | --- | --- |
| Critical | Immediate risk to people, the environment or warranty, or total/material loss of safe operation. | Fire/thermal event, gas, E-stop, ≤2.5 V, full Park outage, safety- related loss of monitoring. |
| Major | Material impact on performance or reliability without an immediate safety threat. | PCS trip, HVAC fault, communication loss, partial outage, monitoring platform unavailable. |
| Minor | Non-critical fault that can be handled on a planned basis. | Minor sensor anomaly or punch-list item with no impact on operation. |
| Informational | Event for trend analysis with no intervention required. | Status change, operating record or diagnostic alert. |

7.2 Operational SLA Target Matrix

The matrix separates notification time, remote response, on-site attendance, safe restoration and permanent resolution. These are operational targets used to organise the O&M service. Liability thresholds, service credits and legal remedies remain exclusively governed by the LTSA and Annex LT-2 unless the Parties expressly agree otherwise in writing.

| Stage | Critical | Major | Minor |
| --- | --- | --- | --- |
| Client Notification | Telephone + e-mail ≤30 min | E-mail ≤2 h | Next Report |
| Acknowledgement / Remote Response | Ack ≤30 min; immediate isolation if required | Remote response ≤4 h | Remote response ≤12 h during working hours |
| On-Site Attendance | ≤4 h if required; safety-critical 24/7 | ≤6 h if required | Next visit or ≤5 business days |
| Restoration Plan | ≤4 h | ≤1 business day | In the work order |
| Safe Restoration | ≤24 h where technically feasible | ≤5 business days | Next visit |
| Permanent Resolution | ≤5 business days unless OEM parts are required | ≤15 business days | Next visit or ≤30 days |
| Status Updates | At least every 2 h until stabilisation | In accordance with the repair plan | In the report / work order |

SLA AND STOP-CLOCK RULES: The Critical on-site attendance target of ≤4 h is an enhanced operational target under this Plan. For Major events, the ≤6 h attendance target does not amend the service-credit threshold in LTSA §8.5. Stop-clock or excluded hours may be applied only to the extent of direct causation, supported by timestamps, correspondence and other evidence, following prompt notification and Client acceptance. Unilateral reclassification of time is not permitted. If a restoration or resolution target cannot be met, a written recovery plan shall be issued stating the reason, revised deadline and risk-mitigation actions.

7.3 Incident Handling Workflow

1.	Detect and retain the alarm source timestamp.

2.	Acknowledge and classify the event and assess the risk to people, warranty and availability.

3.	Apply safe isolation or shutdown where required and authorised.

4.	Notify the Client and the relevant persons in the escalation matrix.

5.	Perform remote diagnosis, secure the logs and open a work order.

6.	Initiate local/OEM/DSO/emergency-services dispatch and confirm site access.

7.	Restore safe partial or full operating capability and document any limitations.

8.	Complete the permanent repair, recommissioning and functional test.

9.	Determine the root cause and define corrective and preventive actions.

10.	Close the incident after evidence acceptance, register updates and submission of the Client report.

7.4 Major Incident

The Major Incident Procedure applies to fire/thermal events, repeated trips, forced outages exceeding 24 hours, cyber incidents, grid-code breaches, warranty-threatening events or unavailable capacity exceeding 10% of a Park.

Client notification - immediately.

Initial incident report - within 24 hours.

Secure logs, photographs, alarms, configurations and witness information.

RCA after stabilisation; the deadline, owner and action plan shall be stated in the initial report.

Provide updates until closure and assess the impact on Availability, SOH, warranty, DSO and insurance.

8.  PREVENTIVE MAINTENANCE PROGRAMME

8.1 Planning Principles

Four quarterly visits per year for each Park, at intervals of approximately three months.

Plan at least 30 days in advance; the preferred low-dispatch window is 04:00-08:00 local time.

Total Scheduled Downtime shall not exceed 48 h per Park per year; exceeding 48 consecutive hours requires the Client's prior written consent, except in a safety emergency.

Container doors shall not be opened during rain, snow, fog, high humidity or excessive wind.

The scope of each activity shall follow the current OEM instructions; stricter requirements shall prevail.

A visit not completed because of weather shall be promptly rescheduled and recorded, without interruption to monitoring continuity.

8.2 Baseline Frequencies

| Frequency | Scope | Owner |
| --- | --- | --- |
| Continuous / Each Shift | Alarms, communications, dispatch, limitations, safety status and handover log. | SCADA / Duty Tech |
| Monthly - Remote | Container status, BMS backup, run-data/parameter/log capture, software review, telemetry and command test. | SCADA |
| Quarterly - Remote | SOH trend, degradation, thermal performance, cell imbalance, communications, data integrity and recommendations. | SCADA + Electrical |
| Quarterly - On Site | Inspection of BESS/PCS/MVS/transformer, thermography, balancing, HVAC, fire systems, connections, relays, sensors, alarms and C5 protection. | Local Team |
| Every 6 Months | Cable screens, SPDs, fuses, copper busbars and connections. | Electrical |
| Annually | Earthing ≤4 Ω, insulation >1 MΩ, protection, SCADA, fire systems, E-stop, SOH/capacity/RTE and cyber-access review. | Discipline Leads + OEM |
| Event-Driven | Alarm, OEM recommendation, serial defect, recall, firmware/regulatory change or trend result. | O&M Manager |

8.3 Scope of the Quarterly Visit

Visual inspection of enclosures, structures, foundations, connections, seals, moisture and contamination.

Thermal imaging of electrical connections and switchgear under an appropriate load condition.

Verification of module balancing, BMS and cell voltages and temperatures.

Inspection and cleaning of cooling systems: filters, fans, intake/outlet, sensors and abnormal noise.

Check readiness of detection/suppression, E-stop, interlocks, signage and fire-service access.

Check cable terminations and tightening torques against OEM values.

Functional test of protection, relays, sensors, meters and communications.

Review of alarms, firmware and OEM-approved updates.

C5 protection: coatings, salt deposits, grilles, seals, drains, surfaces, hinges and fasteners, with photographs.

Restore configuration, complete post-work testing, close doors and confirm monitoring.

8.4 PM Completion Evidence

A work order is considered complete only after attaching the checklist, before/after photographs, measurements, thermograms, tightening torques, test results, parts/consumables list, names and qualifications of personnel, downtime, deviations, recommendations and the verifier's signature.

9.  CORRECTIVE MAINTENANCE AND WORK CONTROL

9.1 CM Scope

Under Tier C, Corrective Maintenance includes diagnosis, labour, travel within Cyprus, safe dismantling and reassembly, configuration restoration, testing, recommissioning and incident documentation for the BESS, PCS, BMS, MVS, SCADA gateway and associated control systems. Parts costs are governed by the warranty, spares and LTSA exclusion provisions.

9.2 Work-Order Control

| Stage | Minimum Data / Gate |
| --- | --- |
| Opening | Number, Park/tag, alarm source, timestamp, class and impact on safety/availability/warranty. |
| Work Plan | Scope, method, risks, LOTO/PTW, PPE, parts, personnel, OEM/DSO approval and rollback plan. |
| Execution | Times, measurements, photographs, parts, serial numbers, configurations before/after and deviations. |
| Post-Repair Test | Protection/interlocks, communications, commands, thermal stability and no active alarms. |
| Restoration | Safe partial/full operation, limitations, post-work monitoring and Client notification. |
| Closure | Cause, CAPA, warranty status, availability coding and updates to the asset/spares/configuration registers. |

9.3 Permit to Work and LOTO

Before work: risk assessment, PTW, identification of energy sources and confirmation of competence and weather conditions.

Before work on a rack, disconnect all MSDs; release locking mechanisms before disconnecting the pack plug.

Each person shall apply their own lock; the de-energised state shall be verified using the appropriate instrument and procedure.

Work near hazardous energy shall be performed only by authorised personnel wearing the required PPE and with a safety observer where required by the risk assessment.

After work: check tools and foreign objects, reconnect MSDs, test interlocks, close doors and have lock owners remove their LOTO devices.

10.  HSE, FIRE SAFETY, ENVIRONMENT AND EMERGENCY RESPONSE

10.1 Overriding Safety Rules

STOP WORK: Every person has the right and duty to stop work in the event of uncontrolled energy, a fire/gas alarm, signs of thermal runaway, inadequate PTW/LOTO/PPE, adverse weather or unclear configuration. Work may resume only after reassessment and authorisation.

Access is restricted to authorised persons; maintain entry/exit records and key control.

Maintain current SDS, OEM instructions, evacuation plan, assembly points and 112/Fire Service contact numbers.

Keep fire-access roads clear, with a minimum width of 6 m.

Keep extinguishers and detection/suppression systems ready and within their inspection dates.

Do not attempt firefighting or open a container during a thermal event except within roles and procedures approved by the OEM and emergency services.

10.2 Response to Fire Alarm / Thermal Event

1.	Do not approach the container or open the doors; warn persons nearby.

2.	Initiate the alarm, evacuation and emergency-services call in accordance with the ERP.

3.	Apply remote E-stop/isolation only where safe and provided for by the procedure.

4.	Provide emergency services with the location, LFP chemistry, SDS, diagram, stored energy, suppression status and possible adjacent hazards.

5.	Secure the zone and 6 m access; do not permit re-entry without approval from the incident commander/HSE.

6.	Preserve logs, monitoring, images and communications; initiate the Major Incident Procedure.

10.3 Environment

Prevent uncontrolled leaks and emissions; respond to spills in accordance with the site plan.

Maintain cooling systems in accordance with F-gas requirements where applicable.

Record and secure damaged batteries, electrical/electronic waste and other hazardous waste and transfer them only to licensed recipients.

Maintain vegetation and remove dry biomass to reduce fire risk without affecting protected areas or environmental conditions.

On plots 71/73, do not interfere with registered stream No. 303; monitor its flow, erosion and signs of contamination and promptly escalate deviations.

Maintain fencing and fauna passages in accordance with approved plans; for plots 471/520, inspect 50 × 25 cm openings spaced every 70-100 m and ensure there are no sharp edges.

Maintain drainage, roads and the site to minimise flooding, corrosion, dust and unauthorised access; do not store materials outside designated areas.

11.  SPARE PARTS, WAREHOUSE AND OBSOLESCENCE

11.1 Local Tier C Warehouse

The Cyprus warehouse shall maintain the agreed minimum stock of critical components sufficient to remedy typical faults within 24 hours. For each item, record the part number, compatibility, application, min/max quantity, condition, location, storage conditions, expiry date, lead time and replenishment deadline.

| Parts Group | Minimum Scope | Control |
| --- | --- | --- |
| BMS / Communications | BMS controllers, communication modules, gateway and sensors. | ESD, firmware/compatibility, test after issue |
| Cooling | Fans, filters, sensors and agreed liquid-cooling components. | Storage conditions, sealing and dates |
| Electrical | Fuses, contactors, SPDs, protection components and minor connections. | Rating, certificates and shelf life |
| PCS | Control boards and agreed power modules. | Model/version and OEM approval |
| Battery | Balancing equipment and OEM-approved parts. | SOC/storage and traceability |
| PM Materials | Filters, cleaning agents, fasteners and protective C5 lubricants. | Min/max and consumption per visit |

The minimum critical-spares list requires written acceptance before PAC and shall identify, for each item, the owner, location, min/max quantity, replenishment deadline and periodic verification method. Full PCS units and transformers need not be stocked unless separately agreed, but the failure strategy shall identify stock, an OEM pool, a replacement unit or a binding lead time. A declared four-week OEM delivery period shall qualify as mitigation only upon presentation of written, binding OEM confirmation. Failure to maintain the agreed stock or critical strategy constitutes Service Provider default, and the resulting downtime shall be classified as Unavailable.

11.2 Replenishment, Warranty Parts and Obsolescence

Issue of a part automatically generates a replenishment reservation/purchase and updates the stock ledger.

A removed part shall be labelled with the fault tag, retained pending the OEM decision and linked to the warranty claim.

Warranty components shall be supplied at no additional cost in accordance with OEM terms; Lighthief shall manage the claim and evidence.

Replacement of major components outside warranty/SOH coverage is subject to a separate quotation.

For at least 15 years, support the availability of compatible parts and firmware; replacements shall be equivalent or better without loss of warranty, certification or grid-code compliance.

12.  AVAILABILITY, SOH, RTE AND WARRANTY MANAGEMENT

12.1 Availability

The contractual Availability guarantee remains as stated in the LTSA: 97% per year at G1+G2 group level. For investor transparency, each Park is also reported separately together with an additional non-binding capacity- weighted group indicator. The additional indicators do not increase the Service Provider's guarantee or liability without a written LTSA amendment.

LTSA CONTRACTUAL FORMULA: Group Availability [%] = SUM(Available Hours per Park) / SUM(Total Hours per Park) × 100. Total Hours are counted for each Park from its PAC: 8,760 h per year or 8,784 h in a leap year, pro rata in the first year.

| Indicator | Calculation Method / Status |
| --- | --- |
| Availability G1 | Reported separately for Galascope 1; diagnostic KPI and basis for remediation. |
| Availability G2 | Reported separately for Galascope 2; diagnostic KPI and basis for remediation. |
| Group Availability LTSA | Contractual hourly indicator calculated in accordance with the LTSA; annual target ≥97%. |
| Capacity-weighted Availability | 100 × [1 - SUM(Unavailable MW × h) / SUM(Rated MW × Total h)]; reporting indicator without separate service credits. |

| Time Category | Rule |
| --- | --- |
| Unavailable | Inability to operate at rated power due to equipment failure, Service Provider-caused downtime, waiting for parts/repair or a culpable SCADA/EMS interface fault. |
| Scheduled Downtime | Previously agreed shutdown; operational limit of 48 h per Park/year. |
| Grid / Curtailment | Excluded where directly caused by a grid/operator instruction and properly documented. |
| Client / Third Party / Force Majeure | Excluded only to the extent of direct causation; the clock is stopped for the documented period. |
| No Dispatch | Does not constitute unavailability if the BESS remains technically capable of operation. |
| EMS/SCADA | Included where the cause is attributable to Lighthief/DISPERON, configuration, integration, gateway, firmware or cyber controls and prevents dispatch/monitoring/DSO operation. |

Each time exclusion from the calculation requires event identification, start and end timestamps, the direct cause, source evidence and Client acceptance. Disputed items remain included until agreed. The monthly report shall list all adjustments, and the annual report shall include joint agreement of the final calculation. If the Availability of either Park falls below 95% in a year, below 97% for two consecutive years, or at least three Critical SLA breaches occur in a 12-month period, the O&M Manager shall initiate a remediation plan, independent technical audit and review of additional stock.

12.2 SOH and Performance Testing

| Year | Minimum SOH - 1 Cycle/Day | Condition |
| --- | --- | --- |
| COD | 98,50% | Initial Reference |
| 1 | 94,62% | OEM curve / operating conditions |
| 2 | 91,77% | OEM curve / operating conditions |
| 3 | 89,91% | OEM curve / operating conditions |
| 4 | 88,00% | OEM curve / operating conditions |
| 5 | 86,78% | Base warranty |
| 10 | 79,58% | Only if the Years 6-10 extension is selected and paid for |
| 15 | 73,61% | Only if the Years 11-15 extension is selected and paid for |

SOH, usable AC capacity and RTE shall be measured at least annually in accordance with the OEM/EPC protocol signed before PAC. The protocol shall unambiguously define the AC measurement point, treatment of auxiliary energy, temperature and tolerance, C-rate, initial and final SOC, rest period, meter calibration, complete required data set, validity criteria and repeat-test rules. The Client and the Lender's Independent Engineer may witness the test. The result shall be delivered as an SOH Certificate and the performance report within 10 business days after the test.

LTSA reference conditions: 20-25°C, full charge/discharge cycle at C/3 and 2 h rest between charge and discharge - to be confirmed against the current OEM protocol before testing.

If the result deviates from the curve, preserve raw data, cycle history, temperatures, power limits, firmware and events that may affect warranty coverage.

The remedy includes parts, labour, installation, recommissioning, testing, documentation and data updates; Lighthief shall actively manage and document the OEM claim.

Annual confirmation of the validity of the OEM warranty reserve, extended warranty, parts availability and support shall form part of the Annual Review.

Any OEM dispute, insolvency risk, supply restriction, recall, safety notice or firmware issue affecting the project shall be reported to the Client within 5 business days.

12.3 Warranty-Preservation File

PM/CM checklists and work orders

photographs and C5 coating condition

torque records

thermograms

earthing and insulation measurements

firmware and configuration register

alarms, SOC and logs

environmental data

fire-system and E-stop tests

parts and traceability

OEM correspondence/claim

SOH/RTE/capacity certificates

personnel qualification evidence

Client/DSO notification evidence

13.  REPORTING, DATA AND CYBERSECURITY

13.1 Reporting Package

| Document | Deadline / Frequency | Minimum Content |
| --- | --- | --- |
| Shift Handover Log | Each Shift | Alarms, limitations, work orders, actions, parts and persons responsible for follow-up. |
| Critical/Major Notification | ≤30 min / ≤2 h | Event, impact, protective actions, ETA and owner. |
| Initial Major Incident Report | ≤24 h | Timeline, safety condition, downtime, data, preliminary cause and RCA plan. |
| Monthly Performance Report | ≤10 business days after month-end | Throughput, G1/G2 Availability, group and capacity-weighted indicators, SOC/SOH, KPIs, alarms, PM/CM, parts and downtime. |
| Quarterly Health Report | ≤15 business days after quarter- end | Degradation, thermal performance, cell imbalance, firmware, recommendations and warranty risks. |
| PM / CM Report | After Each Work Activity | Checklist, results, photographs, measurements, post-work test, punch list and parts. |
| SOH / Performance Report | Annually; ≤10 business days after the test | SOH, usable AC capacity, RTE, protocol, conditions and certificate. |
| Annual Availability Calculation | ≤15 business days after year-end | Per Park, LTSA group and capacity-weighted indicators; included/excluded hours, evidence and LD basis. |
| Annual Review Report | ≤30 days after the PAC anniversary | Benchmark, maintenance, warranties, cybersecurity, spares, regulations and next-year plan. |

Monthly, quarterly and annual reports shall also include raw-data extracts, the incident log, justification of excluded hours, Availability per Park and in aggregate, SOH trend, cell imbalance, thermal deviation, firmware/software versions, open punch items, parts consumption, warranty notices, cyber/security events and recommendations.

13.2 Data Ownership, Access and Retention

The Client owns all operational, technical, market, dispatch, SCADA/BMS/PCS, SOH and Availability data.

The Client shall have continuous secure access to current and historical data and the right to export it at no additional charge.

Retention: at least 15 years from the Commissioning Date and 5 years after termination of the LTSA, in formats accepted by Linyang and the competent authorities.

Client-identifiable data shall not be used for benchmarking, training, product development or third parties without prior written consent.

Documentation shall be delivered in editable format where reasonably available, including settings files, point lists, protocol maps, firmware and certificates.

13.3 ICS Cybersecurity

| Control | Requirement |
| --- | --- |
| Identity | MFA, named accounts, RBAC, least privilege and no shared passwords except for the break-glass account. |
| Remote Access | Encrypted VPN/secure access, approved devices, time-bound access and session logging. |
| Data | Encryption in transit and at rest, configuration backup, restoration testing and integrity control. |
| Changes | Change request, approval, backup, firmware integrity, testing and rollback. |
| Monitoring | Audit logs, access alerts, telemetry loss, anomaly review and retention. |
| Vulnerability Management | Vulnerability register, impact assessment, OEM patches, implementation plan and risk exceptions. |
| Review | Access review at least annually and after each personnel change/incident. |
| Incident | Isolation, evidence preservation, Client notification, RCA and controlled recovery. |

The control framework should align with IEC 62443 principles; the formal scope of IEC 62443 / NIS2 certification shall be confirmed with DISPERON and the ICS suppliers before controlled Rev.2 is issued.

14.  REGULATORY COMPLIANCE, DSO AND COMPETENCE

14.1 Permit, Licence and Lease Register

| Document / Condition | Galascope 1 - 5.0 MWp | Galascope 2 - 2.5 MWp | O&M Control |
| --- | --- | --- | --- |
| CERA/RAEK operating exemption | E2674/2020; 14.04.2020-13.04.2050 | E2673/2020; 14.04.2020-13.04.2050 | Annual review; apply for extension at least 3 months before expiry. |
| EOA approval certificate | P1 139876 dated 25.02.2026; certificate noting a container on plot 73. | P1 139841 dated 25.02.2026; PV completion confirmed in accordance with the permits. | Protect the approved configuration; maintain a register of deviations and approvals. |
| BESS submission 2026 | Designer declaration and plots 71/73 plans dated April 2026. | Designer declaration and plots 471/520 plans dated April 2026. | Obtain final EOA approval/acceptance and stamped drawings; update after any change. |
| Lease / land right | Lease from 01.11.2018 to 2039; right to two five-year extensions. | Leases from 01.11.2018 to 2039; renewal rights in accordance with the agreements. | Annual review; alerts 24/12/6 months before the required action date. |
| Decommissioning | Remove the installation at end of life; the fencing remains with the owner; permit conditions require site reinstatement. | Remove the installation and reinstate the site; the permit specifies a deadline of 6 months after PV operation ceases. | Maintain a current decommissioning plan, cost estimate and materials/waste register. |

REGULATORY CHANGE CONTROL: Modification of the plant requires the applicable permit/licence amendment; expansion requires a new building/regulatory procedure. A change of ownership requires an application to CERA/RAEK at least 3 months in advance. Disposal of or creation of security over a material asset with replacement value above EUR 200,000 requires at least one month's prior notice and the applicable consent/no objection. A planned closure shall be notified at least 12 months in advance where circumstances permit.

14.2 Site Obligations from EOA Documentation

| Area | Control Requirement | Frequency / Evidence |
| --- | --- | --- |
| Access and EAC | Keep roads, gates, parking, access strips and routes to EAC rooms/substations clear throughout the year. | Each visit; photographs and work orders for defects. |
| Fencing / Fauna | Maintain the 2.10 m fence free of damage; keep fauna passages clear, without sharp edges or trapping hazards. | Quarterly and after storms/events. |
| Drainage / Stream | Keep drains and channels clear; no erosion, ponding or contamination; no interference with stream No. 303. | Quarterly and after heavy rain. |
| Fire Safety / Vegetation | Remove dry biomass, keep fire-access roads clear, maintain extinguishers and systems ready and cooperate with the Fire Service. | Monthly during the dry season; each visit. |
| Waste | Transfer WEEE, batteries, oils/coolants and other waste only to licensed entities; maintain a complete transfer record. | For each consignment; quarterly report. |
| Site Security | Maintain CCTV, laser barriers, lighting, locks and lightning protection operational; no unauthorised structures. | Monthly remotely / quarterly on site. |
| Approved Configuration | Containers, foundations, roads and equipment located in accordance with stamped drawings/as-built documentation. | After changes and during the annual audit. |

14.3 Testing and Operational Obligations

| Area | Activity | Frequency / Deadline |
| --- | --- | --- |
| Protection | Test all protection-relay functions. | Annually |
| Earthing | Measure resistance; result ≤4 Ω. | Annually |
| Insulation | Measure insulation resistance; result >1 MΩ. | Annually |
| SCADA | Verify P, Q, V, I, f, SOC and SOH signals and the IEC 60870-5-104 link. | Annually + continuous monitoring |
| Control | Test P-set, Q-set, start/stop and zero-export, if applicable. | Monthly |
| Power quality | Availability of PQDIF and COMTRADE data. | Continuous / after an event |
| Fire Safety | Detection, suppression, pressure, E-stop and extinguishers. | Each visit / as required by law |
| Permit / Lease Register | Status of EOA/CERA approvals, conditions, leases, designer insurance and renewal dates. | Quarterly + deadline alerts |
| Site | Access, gates, fencing, fauna passages, drainage, stream, CCTV/lighting and waste. | Each visit / after an event |
| DSO Planned Outage | Notification of the planned outage. | At least 7 days in advance |
| DSO Fault | Fault report within 24-48 h; emergency outage notified immediately by telephone + e-mail. | Event-Driven |
| Authority Inspection | Provide personnel and documents within 5 business days and close findings. | On request |

The regulatory basis has been adopted in accordance with the LTSA: the laws of Cyprus, EAC Technical Guide for Storage 2025, EAC Universal Technical Guide for RES 2025 and fire-safety and environmental requirements. Before controlled Rev.2 is issued, confirm that all legal and technical references are current and applicable.

14.4 Qualifications and Training

Current Cypriot electrical authorisations/competence appropriate to the work scope.

Linyang OEM training on the BESS, BMS, warranty limitations and maintenance manual.

Training on PCS/MVS, EMS/SCADA, IEC 60870-5-104 and approved settings.

HSE: HV/LV safety, LOTO/PTW, arc flash/PPE according to the risk assessment, work near batteries and first aid.

Fire and emergency response, including drills with the local Fire Service and knowledge of SDS.

Cybersecurity and secure remote access; refresher training after a system change/incident.

15.  QUALITY, AUDITS AND IMPROVEMENT

15.1 Management KPIs

| KPI | Control Method | Target / Trigger |
| --- | --- | --- |
| Group Availability LTSA | Monthly and annually; G1+G2 weighted by hours. | ≥97% annually - contractual guarantee |
| Park Availability | G1 and G2 separately; monthly and rolling 12 months. | <95%/year triggers remediation |
| Capacity-weighted Availability | 1 - SUM(Unavailable MW × h) / SUM(Rated MW × total h). | Reporting only; no separate service credits |
| Critical acknowledgement | From alert timestamp to acknowledgement. | ≤30 min |
| SLA restoration/resolution | Clock with documented stop-clock periods. | 100% or an accepted deviation plan |
| PM completion | Completed on time / planned. | 100% of OEM-required tasks |
| Overdue actions | Open CAPA/punch/warranty items. | 0 overdue Critical/Major items |
| Warranty evidence | Completeness of the Warranty File. | 100% of work orders with evidence |
| Spare stock compliance | Items at or above minimum stock and within storage conditions. | 100%; replenishment by the deadline |
| Cyber access review | Accounts, permissions and sessions. | At least annually and after a change |
| Safety | Incidents, near misses and actions. | Zero recordable incidents; 100% closure |

15.2 Audits and CAPA

Quarterly review of data quality, downtime classification, work orders and evidence completeness.

Annual audit of compliance with OEM requirements, warranty, spares, cybersecurity, qualifications, DSO requirements and documentation.

Each Critical incident, repeated service failure or warranty non-compliance triggers RCA and CAPA.

Each CAPA shall have an owner, deadline, effectiveness evidence and closure approval.

The Client and the Lender's Independent Engineer shall have access to agreed evidence and may witness tests.

16.  SERVICE COMPLETION AND HANDOVER

Upon LTSA expiry or termination, Lighthief shall provide up to 90 days of transition assistance at agreed rates to preserve safe operation, warranties and full knowledge transfer.

Export all data and logs in the agreed format.

Transfer passwords and access credentials through a secure channel; rotate them after receipt.

Configuration files, point lists, register maps and firmware versions.

PM/CM registers, measurements, thermograms, certificates, photographs and Warranty Files.

Open incidents, CAPA, punch items, restrictions and schedules.

Parts list, stock ledger, storage conditions and open purchase orders.

Warranty claims, OEM correspondence and extended-warranty status.

Joint handover review and Client-approved handover record.

Appendix A.  APPENDIX A - ANNUAL MAINTENANCE MATRIX

The matrix is the minimum schedule. Current OEM instructions, monitoring results, regulations and warranty conditions may require more frequent or broader activities.

| Activity | Cont. | Monthly | Quarterly | 6 Months | Year | Event- Driven |
| --- | --- | --- | --- | --- | --- | --- |
| Alarms / Telemetry / Connectivity | X | X | X |  | X | X |
| BMS backup / logs / parameters |  | X | X |  | X | X |
| Remote command verification |  | X |  |  | X | X |
| SOH / cell imbalance / thermal trend | X | X | X |  | X | X |
| Container / seals / moisture / C5 |  |  | X |  | X | X |
| HVAC / liquid cooling / filters | X | X | X |  | X | X |
| Thermal imaging |  |  | X |  | X | X |
| Cable shielding / SPD / fuses / busbar |  |  |  | X | X | X |
| Torque verification |  |  | X |  | X | X |
| Grounding ≤4 Ω / bonding |  |  |  |  | X | X |
| Insulation resistance >1 MΩ |  |  |  |  | X | X |
| Protection relays / switchgear |  |  | X |  | X | X |
| Fire detection / suppression / E-stop | X |  | X |  | X | X |
| SCADA signal / IEC 104 / PQ data | X | X | X |  | X | X |
| SOH / AC capacity / RTE test |  |  |  |  | X | X |
| Cyber access / backup restore review | X | X | X |  | X | X |
| Spares stock / shelf life |  | X | X |  | X | X |
| Vegetation / drainage / access roads |  |  | X |  | X | X |
| Fence / fauna passages / gates |  |  | X |  | X | X |
| CCTV / laser barriers / lighting | X | X | X |  | X | X |
| Registered stream no. 303 - G1 |  |  | X |  | X | X |
| Permit / licence / lease register |  |  | X |  | X | X |
| Waste transfer records |  |  | X |  | X | X |

Appendix B.  APPENDIX B - QUARTERLY ON-SITE VISIT CHECKLIST

For each item, enter the result: OK / NOK / N/A, evidence and work-order number. Absence of evidence means completion is not confirmed.

| Area | Inspection Point | Result | Evidence / WO |
| --- | --- | --- | --- |
| Safety | Acceptable weather; PTW/LOTO/PPE; safe opening; MSD and pack plug in accordance with OEM instructions. |  |  |
| Container | No damage, corrosion, deformation, combustible materials, moisture or foreign objects. |  |  |
| Foundation / Doors | Fixings free of corrosion, lock operational, seals intact and doors closing correctly. |  |  |
| Airflow | Intakes, outlets and ventilation paths clear. |  |  |
| Cables | No damage, correct routing, sealed entries, no looseness or short-circuit risk. |  |  |
| Connections | Torque to OEM values; terminal insulation, screens, busbars, SPDs and fuses in correct condition. |  |  |
| Switchgear / Relays | Switchgear operation, settings, interlocks and protection test. |  |  |
| Thermography | Connections, switchgear, PCS, busbars and anomalies documented. |  |  |
| Earthing | Connections and bonding correct; annual measurement ≤4 Ω. |  |  |
| Battery | Visual inspection of modules, cell V/T, balancing, BMS communications and SOH. |  |  |
| Thermal Systems | HVAC/liquid cooling, fans, filters, noise, sensors and performance. |  |  |
| Fire Safety | Suppression ready/pressure OK, detectors, E-stop, interlocks, ventilation and signage. |  |  |
| Data | BMS/run/parameters/logs saved; firmware, update, communications and monitoring verified. |  |  |
| C5 / Coastal Environment | Coatings, salt, grilles, seals, drains, surfaces, hinges and fasteners; photographs. |  |  |
| Access / Gates | Roads, parking, 4 m/6 m gates and access for EAC/emergency services clear; no obstructions or damage. |  |  |
| Fencing / Fauna | 2.10 m fencing complete; fauna passages clear, with no sharp edges or signs of trapped animals. |  |  |
| Drainage / Stream | Drains and channels clear; no erosion or ponding; at G1 no interference with or contamination of stream No. 303. |  |  |
| Security | CCTV, laser barriers, lighting, locks and lightning protection operational; test and evidence. |  |  |
| Vegetation / Waste | Dry biomass removed; no uncontrolled waste; transfer documents for a licensed recipient. |  |  |
| EOA / as-built | No new structures or location changes outside the approved plan; every difference entered in the Permit Register. |  |  |
| After Work | MSDs connected, tools removed, system operational and doors/seals/locks checked. |  |  |
| Documentation | Log, photographs, measurements, parts, recommendations, punch list and report complete. |  |  |

Appendix C.  APPENDIX C - ALARM AND ESCALATION MATRIX

| Event | Class | Initial Action / Escalation | Client |
| --- | --- | --- | --- |
| Fire / Gas / Thermal Event | Critical | Isolation, evacuation, 112, Client, HSE, OEM | Immediately |
| Cell voltage ≤2,5 V | Critical | Protection/isolation, Client, OEM, warranty incident | Immediately |
| Cell voltage <2,9 V / low SOC | Critical if warranty- threatening | Recharge plan, Client, OEM if the condition worsens | ≤30 min |
| Full Park Outage | Critical | Diagnosis, dispatch, plan ≤4 h, update every ≤2 h | ≤30 min |
| PCS trip / >10% unavailable capacity | Major / Major Incident | Client, Electrical Lead, OEM; report ≤24 h if >10% | ≤2 h |
| HVAC/liquid cooling fault | Major or Critical depending on temperature | Operating limitation, HVAC dispatch, thermal monitoring | ≤2 h / ≤30 min |
| Monitoring platform failure | Major; Critical if safety-related | Backup channel, SCADA/IT dispatch, Client | ≤2 h / ≤30 min |
| Communication / DSO Telemetry Loss | Major | Gateway/EMS/SCADA, DSO if required, availability coding | ≤2 h |
| Cyber Incident | Critical / Major Incident | Logical isolation, Client, evidence preservation, recovery | Immediately |
| Minor Sensor / Cosmetic Defect | Minor | WO; next visit or ≤30 days | Next Report |

Appendix D.  APPENDIX D - MINIMUM FIELDS FOR REGISTERS AND REPORTS

| Register | Minimum Fields |
| --- | --- |
| Work Order | ID, Park/tag, alarm, class, timestamp, owner, scope, LOTO/PTW, parts, times, results, test, downtime coding and closure. |
| Incident Log | Timeline, severity, notifications, safety state, unavailable capacity, evidence, RCA/CAPA, warranty/DSO/insurance impact. |
| Downtime Log | Start/stop, Park, affected MW/MWh, included/excluded, causal evidence, stop-clock, reviewer and Client challenge. |
| Spares Ledger | Part number, compatibility, serial/lot, min/max, stock, location, storage, shelf life, issue/return, reorder deadline. |
| Configuration Register | System/tag, setting/version before/after, approver, backup, test, rollback, DSO/OEM reference. |
| Warranty Register | OEM, scope, start/end, extension, claim, evidence, status, deadlines, reserve/support confirmation. |
| Training Matrix | Person, role, qualification, OEM/HSE/SCADA/cyber training, validity and refresher due date. |
| Contact Matrix | Role, person, telephone/e-mail, deputy, coverage, escalation level, language and contact test. |
| Permit & Lease Register | Park, document, number, authority/party, scope, issue/expiry, conditions, alert, owner, status and evidence. |
| Environmental & Waste Register | Event/waste, code and quantity, location, recipient/licence, transfer record, spill, actions and photographs. |

EOA DOCUMENTS AND LAND-RIGHTS REGISTER

The following section supplements Appendix D and describes the source package provided on 07.08.2026. The Greek-language originals remain the governing documents; the summaries in this Plan are intended for operational control of obligations.

| ID | Asset | Document | Key Data | O&M Status |
| --- | --- | --- | --- | --- |
| G1-01 | 5.0 MWp / 71 and 73 | Designer declaration for the BESS/data-centre procedure - Special Exemption Order 2026 | Andreas Papaiacovou Architects L.L.C.; policy dated 28.04.2026 | Open - confirm validity and EOA acceptance |
| G1-02 | 5.0 MWp / 71 and 73 | BESS Site-Layout and Foundation Plans | April 2026; scale 1:2000; C35/B420C | To be replaced with stamped/as-built drawings after approval |
| G1-03 | 5.0 MWp / 71 and 73 | EOA Certificate of Approval with Notes | P1 139876 dated 25.02.2026 | Note: container on plot 73 |
| G1-04 | 5.0 MWp / 71 and 73 | Long-Term Lease Agreement | 02.11.2018; initial term to 2039; 2 × 5-year renewals | Active - monitor deadlines |
| G1-05 | 5.0 MWp / 71 and 73 | Building Permit and Environmental Conditions | Permit 052161; environmental documentation and EOA conditions | Conditions included in checklists |
| G1-06 | 5.0 MWp / 71 and 73 | CERA/RAEK operating exemption | E2674/2020; 14.04.2020-13.04.2050 | Active - 5.0 MWp PV |
| G1-07 | 5.0 MWp / 71 and 73 | Property Titles | 0/3190 and 0/3189; Foinitzi, Avgorou | Source of plot data |
| G1-08 | 5.0 MWp / 71 and 73 | Cadastral Plan | Plans 2-278-381 and 2-278-382; section 12 | Source of boundaries and stream data |
| G1-09 | 5.0 MWp / 71 and 73 | Power of Attorney | 02.11.2018; N.S.P.S. Plantations Limited | Historical document for the PV procedure |
| G2-01 | 2.5 MWp / 471 and 520 | Designer declaration for the BESS/data-centre procedure - Special Exemption Order 2026 | Andreas Papaiacovou Architects L.L.C.; policy dated 28.04.2026 | Open - confirm validity and EOA acceptance |
| G2-02 | 2.5 MWp / 471 and 520 | BESS Site-Layout and Foundation Plans | April 2026; scale 1:1000; C35/B420C | To be replaced with stamped/as-built drawings after approval |
| G2-03 | 2.5 MWp / 471 and 520 | EOA Certificate of Approval | P1 139841 dated 25.02.2026 | PV completed in accordance with the permits |
| G2-04 | 2.5 MWp / 471 and 520 | Long-Term Leases | Agreements/registers from 01.11.2018 to 2039 | Active - monitor deadlines |
| G2-05 | 2.5 MWp / 471 and 520 | Building Permit and Conditions | Permit 052065; file B80/2015 | Road, drainage, fencing and EAC conditions |
| G2-06 | 2.5 MWp / 471 and 520 | CERA/RAEK operating exemption | E2673/2020; 14.04.2020-13.04.2050 | Active - 2.5 MWp PV |
| G2-07 | 2.5 MWp / 471 and 520 | Property/Lease Titles | 0/7249 and 0/7864; Kerimis, Avgorou | Source of plot data |
| G2-08 | 2.5 MWp / 471 and 520 | Cadastral Plans | Plan 2-278-381; section 03 | Source of boundaries and access data |
| G2-09 | 2.5 MWp / 471 | Power of Attorney | 02.11.2018; Dinos Konstantinou | Historical document for the PV procedure |

END OF DOCUMENT