## Financial
BESS (financial)
Project name | Larnaca Cyprus
Max power | 50 MW
Rated voltage (POC) | 132kV
Guaranteed energy capacity | 100 MWh
Lighthief
System | Type [Oversized/ Augmentation] | - | Oversized + Augmentation — 5x T8 @ 10MW (50MW POC); 24x 5MWh containers (120MWh nameplate); CONFIRM: 20 BESS @ 2:1 PCS ratio at COD + 4 aug, or 6th T8 skid
Time of augmentation
| Nameplate DC capacity | MWh | 120.36
| Usable DC capacity (after SAT) | MWh | TBC — post-SAT measured (target >=100 MWh @ POC)
| Usable AC capacity at POC (after SAT) | MWh | 100
| Usable DC capacity (after 10 years) | MWh | TBC — degradation model + augmentation modules
| Usable AC capacity at POC (after 10 years) | MWh | >100 (contractual guarantee)
| DC containers number | - | 24
| Skid enclosure | YES/NO | YES
| Skids containers number |  | 5
Total costs | Basic cost - Batteries | € | TBC — pending commercial offer
| Basic cost - Skid | € | TBC — pending commercial offer
| Transportation costs | € | TBC — pending commercial offer
| Installation & commissioning costs | € | TBC — pending commercial offer
| Import taxes | € | TBC — pending commercial offer
| Total CapEx | € | TBC — pending commercial offer
| Total CapEx cost | €/MWh | TBC — pending commercial offer
| Product & Perform. warranty [Y1-2] | € | TBC — pending commercial offer
| Product & Perform. warranty [Y3] | € | TBC — pending commercial offer
| Product & Perform. warranty [Y4-Y10] | € | TBC — pending commercial offer
| Corrective maintenance [Y1-Y10] | € | TBC — pending commercial offer
| Preventive maintainance [Y1-Y10] | € | TBC — pending commercial offer
| Spare parts [Y1-10] | € | TBC — pending commercial offer
| Total Opex | € | TBC — pending commercial offer
| Total Opex | €/MWh | TBC — pending commercial offer
| Battery recycling costs | € | TBC — pending commercial offer
Counterparties | Supply |  | Linyang Energy (battery) + Kehua (PCS/skid) via Lighthief Cyprus Ltd
| SLA |  | Lighthief Cyprus Ltd — LTSA available Y1-10
Production place & FATs |  |  | Jiangsu, China (Linyang) / Xiamen, China (Kehua)
Delivery terms | Place |  | Larnaca, Cyprus
| Type |  | DDP Larnaka
Delivery time | Production time |  | ~90 days production (per OEM lead time)
| Transport time |  | ~50 days shipping CIF + local transport
Product Waranty | Product waranty DC part |  | 3 years DC minimum per RfP (Linyang standard 5yr base available)
| Product waranty AC part |  | 3 years AC (PCS + MV skid)
| Performance waranty |  | Performance warranty per Linyang terms — SOH curve attached
O&M | Spare parts availability |  | Yes — critical spares list available on request
| Spare parts costs |  | TBC
| Service team (local, …) |  | Cyprus-based service team (Lighthief) + OEM remote support
Reference projects | Greece |  | Greece: Athalassa 40MW/80MWh, Anatoliko 40MW/160MWh, FIZ 40MW/160MWh
| Europe |  | Cyprus: Lighthief BESS portfolio — Linyang/Kehua (249 MW pipeline)
Offer | Date |  | 2026-05-27
| Validity |  | 30 days
Contact | Person |  | Alexander Papacosta
| E-mail |  | office@lighthief.com

## Technical
BESS (technical)
Project name | Larnaca Cyprus
Max power | 50 MW
Rated voltage (POC) | 132kV
Guaranteed energy capacity | 100 MWh
|  |  | Lighthief | Ex work | Delivery at factory
|  |  |  | DAP | Delivered at place
System | Type [Oversized/ Augmentation] | - | Oversized + Augmentation — 5x T8 @ 10MW (50MW POC); 24x 5MWh containers (120MWh nameplate); CONFIRM: 20 BESS @ 2:1 PCS ratio at COD + 4 aug, or 6th T8 skid | DDP | Delivered Duty Paid
| Nominal Capacity (DC) - Nmaeplate | MWh | 120.36
DC container | Number of containers |  | 24
| Technology |  | LFP (LiFePO4) — EVE 314Ah prismatic cells
(battery) | Capacity per container | kWh | 5015
| DC Voltage rated | V | 1331.2
| DC Voltage range | V | 1164.8 – 1497.6
| Operating profile | cycle/ day | 1.5
| Allowed C-rate |  | 0.5C standard / 1C max (cell spec)
| Noise sound @1m | dB | TBC — request factory test report
| Temperature range anbient | ° C | -30 to +50 (container); -10 to +45 @ full power per TSOC
| Humidity |  | <95% RH non-condensing
| Level of protection |  | IP54
| Anti-corrosion class |  | C5
| Cooling type |  | Liquid cooling (45 kW unit)
| Auxiliary consumption | kW | 45
| Fire protection system |  | Aerosol + off-gas detection (H2, CO) + backup water sprinkler
| Lifetime | years | 15
|  | cycles | 6000
| Weight | tn | 43
| Dimensions (LxWxH) | mm | 6058 x 2438 x 2896
Skid mounting | Skid enclosure (YES/NO) |  | YES
| Skids number |  | 5
| Technology |  | Kehua BCS10000K-C-HUD/T8
| Weight | tn | 38
| Dimensions (WxDxH) | mm | 12192 x 2896 x 2438
PCS (DC to AC) | Manufacturer & Model |  | Kehua (Xiamen Kehua Digital Energy Tech Co., Ltd) / Kehua BCS1250K-C-HUD
| Number | - | 40
| Nominal power | kW | 1250
| Weight | kg | 950
| Dimensions (WxDxH) | mm | 735 x 2135 x 1300
Transformers | Manufacturer & Model |  | Kehua / Kehua SL-10000
| Number |  | 5
| Rated power |  | 10,000 kVA
| Nominal voltage ratio |  | 0.69/33 kV (custom)
Switchgear | Manufacturer & Model |  | Schneider RM AirSeT 24kV SF6-free
| Number |  | TBC — qty per SLD
| Nominal voltage | kV | 33
| Nominal operating current | A | TBC — per protection study
Notes
Notes | Training |  | On-site training included (commissioning scope)

## Other
BESS (other)
Lighthief
Cells | Model |  | EVE LF314
| Chemical composition |  | LFP (LiFePO4)
| Rated Energy | kWh | 1004.8
| Rated Voltage | V | 3.2
| Operating Voltage range | V | 2.5 – 3.65
| Cell weight | kg | 5.5
| Cell dimensions (W x D x H) | mm | 72 x 174 x 207.7
Modules | Model |  | 1P104S Battery Pack
| Configuration |  | 1P104S (104 cells series)
| Rated Energy | kWh | 104.499
| Rated Voltage | V | 332.8
| Operating Voltage range | V | 291.2 – 374.4
| Weight | kg | 690
| Dimensions (W x D x H) | mm | 762.5 x 2180 x 252
Container | Model |  | Linyang Power Atlantic ME 5.015 MWh (20HC)
| Configuration |  | 12P416S (12 racks x 1P416S)
| Rated Energy | kWh | 5015
| Rated Voltage | V | 1331.2
| Operating Voltage range | V | 1164.8 – 1497.6
| Weight | kg | 43000
| Dimensions (W x D x H) | mm | 6058 x 2438 x 2896
| Modules per container |  | 48
| Racks per container |  | 12
| Modules per rack |  | 4