## Version history
Three-phase Power Conversion System BCS1250K-C-HUD(V1.0) Northbound Monitoring Modbus Communication Protocol(V1.00A)
WRDF-0I002-103/001
Version history
Protocol version | Document version | Revision time | Revision content | Revision person
V1.00A | 001 | 2025.08.13 | First release | KH00730

## Protocol overview
1 | General rule
This protocol is applicable for the communication between host and slave, the host requires data from the slave circularly, the slave receives the request command and responds corresponding data.
This protocol is based on Standard Modbus Protocol.
2 | Related Terms and Description
| Name | Description
| Host | The part that initiatively start to communicate
| Slave | The part that passively respond the command
| UINT16 | Unsigned integer of 16 bit. High byte front, low byte behind
| ENUM | Unsigned integer of 26 bit.. Data enumeration format.
| UINT32 | Unsigned integer of 32 bit. High byte front, low byte behind
| INT16 | Signed integer of 16 bit. High byte front, low byte behind
| INT32 | Signed integer of 32 bit. High byte front, low byte behind
| String | Character string that every byte marked by ASCII
| MLB | Multibyte
| Bitfield16 | The data that with 16-bit width and shows by bit. High byte front, low byte behind
| RW | The register that can be read and written
| RO | The register that can be read only
| WO | The register that can be written only
3 | Related Terms and Description
| 1. Communication Configuration of RS485 Port |  |  |  |  | 1.Communication Configuration of Ethernet Port
| Name | Description |  |  |  | Name | Description
| Transmission mode | RTU |  |  |  | Transmission mode | TCP/IP
| Baud rate | Default is 9600bps, and it can be set to 4800bps, 9600bps, 19200bps, 38400bps |  |  |  | Baud rate | 10M/100M
| Start bit | 1bit |  |  |  | Port ID | 502
| Data bit | 8bits |  |  |  | Max. response time of the slave | 10ms
| Parity bit | None |  |  |  | Min. polling interval of the host | 10ms
| Stop bit | 1bit |  |  |  | IP | Default: 192.168.1.10
| Frame interval | Not less than the transmission time of 3.5 bytes |  |  |  | Subnet mask | Default: 255.255.255.0
| Intra-frame character interval | Not larger than the transmission time of 1.5 bytes |  |  |  | Gateway | Default: 192.168.1.1
| Max. frame length | 200 bytes
| Max. response time of the slave | The transmission time of 150 bytes
| Min. polling interval of the host | The transmission time of 200 bytes
4 | Function Code Description
| No. | Function code |  | Meaning |  | Remark
| 1 | 0x01 |  | Read by byte
| 2 | 0x02 |  | Read by byte
| 3 | 0x03 |  | Read by word
| 4 | 0x04 |  | Read by word
| 5 | 0x05 |  | OFF-0x0000; ON-0xFF00
| 6 | 0x06 |  | Write by word
| 7 | 0x10 |  | Write by word
| 8 | 0xE0 |  | Write by word
5 | ModbusRTU Instruction Details
5.1 Read holding registers (Function Code:0x03)
Host request (Hexadecimal)
| ID | Function code | Register starting address |  | Quantity |  |  | CRC16
|  |  | High byte | Low byte | High byte | Low byte |  | Low byte |  | High byte
| xx | 0x03 | xx | xx | xx | xx |  | xx |  | xx
Slave response (Hexadecimal)
| ID | Function code | Register 1 |  | ... |  |  | Register N |  |  |  | CRC16
|  |  | High byte | Low byte | ... | ... |  | High byte |  | RegLen | Low byte | Low byte |  | High byte
| xx | 0x03 | xx | xx | ... | ... |  | xx |  | xx |  | xx |  | xx
Description
Reading one or more registers is distinguished by the quantity of register. If the quantity of register is 1, it means that there is one register. If the quantity of register is more than 1, it means that there are several registers. Register 1 is corresponding to the starting address.
5.2 Read input registers (Function Code:0x04)
Host request (Hexadecimal)
| ID | Function code | Register starting address |  | Quantity |  |  | CRC16
|  |  | High byte | Low byte | High byte | Low byte |  | Low byte |  | High byte
| xx | 0x04 | xx | xx | xx | xx |  | xx |  | xx
Slave response (Hexadecimal)
| ID | Function code | Register 1 |  | ... |  |  | Register N |  |  |  | CRC16
|  |  | High byte | Low byte | ... | ... |  | High byte |  | RegLen | Low byte | Low byte |  | High byte
| xx | 0x04 | xx | xx | ... | ... |  | xx |  | xx |  | xx |  | xx
Description
Reading one or more registers is distinguished by the quantity of register. If the quantity of register is 1, it means that there is one register. If the quantity of register is more than 1, it means that there are several registers. Register 1 is corresponding to the starting address.
5.3 Preset Single Register (Function Code:0x06)
Host request (Hexadecimal)
| ID | Function code | Register starting address |  | Register setting value |  |  | CRC16
|  |  | High byte | Low byte | High byte | Low byte |  | Low byte |  | High byte
| xx | 0x06 | xx | xx | xx | xx |  | xx |  | xx
Slave response (Hexadecimal)
| ID | Function code | Register starting address |  | Register setting value |  |  | CRC16
|  |  | High byte | Low byte | High byte | Low byte |  | Low byte |  | High byte
| xx | 0x06 | xx | xx | xx | xx |  | xx |  | xx
5.4 Preset Multiple Registers (Function Code:0x10)
Host request (Hexadecimal)
| ID | Function code | Register setting start address |  | Register setting quantity(N) |  |  | Byte quantity | Register setting value |  |  |  | Register... | CRC16
|  |  | High byte | Low byte | High byte | Low byte |  | 2*N | High byte |  | Low byte |  | ... | Low byte | High byte
| xx | 0x10 | xx | xx | xx | xx |  | xx | xx |  | xx |  | ... | xx | xx
Slave response (Hexadecimal)
| ID | Function code | Register address |  | Reset register quantity |  |  | CRC16
|  |  | High byte | Low byte | High byte | Low byte |  | Low byte |  | High byte
| xx | 0x10 | xx | xx | xx | xx |  | xx |  | xx
5.5 Error Information and Data Processing
Slave response (Hexadecimal)
| ID | Function code | Error code | CRC16
|  |  |  | Low byte | High byte
| xx | xx¦0x80 | xx | xx | xx
Description
When the communication module of slave detects error except CRC error, it must send the information to the host. The highest bit of function code is 1, that is, add 128 at the sent function code of host. The responded and sent error codes of slave's communication module are as follows.
| Error code | Description |  | Remark
| 0x01 | Invalid function code |  | The server does not understand the function code
| 0x02 | Invalid data address |  | Related to the request
| 0x03 | Invalid data value |  | Related to the request
| 0x04 | Service fault |  | The communication module of slave cannot take out the data fault during processing
| 0x10 | Wrong register setting value |  | Password mismatch, setting exceed setting range, etc.
| 0x11 | No authority
6 | Modbus TCP Instruction Details
A special header used on the TCP/IP is to indentify Modbus application data unit, called MBAP header (Modbus protocol header).
The difference between Modbus TCP data frame and serial link data frame:
MBAP header includes the following fields:
| Field | Length | Description | Client | Server
| Transaction ID | 2 byte | Modbus request response transaction processing ID | Client start | Server recopies from the received request
| Protocol ID | 2 byte | 0: Modbus protocol | Client start | Server recopies from the received request
| Length | 2 byte | Number of bytes | Client start (request) | Client (response) start
| Unit ID | 1 byte | The ID of the remote slave connected to the serial link or other bus | Client start | Server recopies from the received request
Description
Header length is 7 bytes:
Transaction processing ID: Used for transaction matching. In response, the Modbus server copies the transaction processing ID of the request.
Protocol ID: Used for multiplexing within system. The Modbus protocol is identified by a value of 0.
Length: The length filed is the number of bytes in the next field, including unit ID and data field.
Unit ID: This field is used for intra-system routing. Dedicated to communication between Modbus or Modbus+ serial link slaves by a gateway between an Ethernet TCP-IP network and a Modbus serial link. The Modbus client sets this field in the request, and the server must return this field with the same value in the response.
All Modbus/TCP ADUs are sent through TCP on the registered port 502.
6.1 Read holding registers (Function Code:0x03)
Request PDU
| Function code | Register starting address |  | Register quantity
|  | High byte | Low byte | High byte | Low byte
| 0x03 | xx | xx | xx | xx
Response PDU
| Function code | Register 1 |  | ... |  |  | Register N
|  | High byte | Low byte | ... | ... |  | High byte |  | Low byte
| 0x03 | xx | xx | ... | ... |  | xx |  | xx
Description
Reading one or more registers is distinguished by the quantity of register. If the quantity of register is 1, it means that there is one register. If the quantity of register is more than 1, it means that there are several registers. Register 1 is corresponding to the starting address.
6.2 Read input registers (Function Code:0x04)
Request PDU
| Function code | Register starting address |  | Register quantity
|  | High byte | Low byte | High byte | Low byte
| 0x04 | xx | xx | xx | xx
Response PDU
| Function code | Register 1 |  | ... |  |  | Register N
|  | High byte | Low byte | ... | ... |  | High byte |  | Low byte
| 0x04 | xx | xx | ... | ... |  | xx |  | xx
Description
Reading one or more registers is distinguished by the quantity of register. If the quantity of register is 1, it means that there is one register. If the quantity of register is more than 1, it means that there are several registers. Register 1 is corresponding to the starting address.
6.3 Preset Single Register (Function Code:0x06)
Request PDU
| Function code | Register starting address |  | Register setting value
|  | High byte | Low byte | High byte | Low byte
| 0x06 | xx | xx | xx | xx
Response PDU
| Function code | Register starting address |  | Register setting value
|  | High byte | Low byte | High byte | Low byte
| 0x06 | xx | xx | xx | xx
6.4 Write Multiple Registers (Function Code:0x10)
Request PDU
| Function code | Register setting start address |  | Register setting quantity(N) |  |  | Byte quantity | Register setting value |  |  |  | Register ...
|  | High byte | Low byte | High byte | Low byte |  | 2*N | High byte |  | Low byte |  | ...
| 0x10 | xx | xx | xx | xx |  | xx | xx |  | xx |  | ...
Response PDU
| Function code | Register address |  | Reset register quantity
|  | High byte | Low byte | High byte | Low byte
| 0x10 | xx | xx | xx | xx
6.5 Error Information and Data Processing
Response PDU
| Function code | Error code
| xx¦0x80 | xx
Description
When the communication module of slave detects error except CRC error, it must send the information to the host. The highest bit of function code is 1, that is, add 128 at the sent function code of host. The responded and sent error codes of slave's communication module are as follows.
| Error code | Description |  | Remark
| 0x01 | Invalid function code |  | The server does not understand the function code
| 0x02 | Invalid data address |  | Related to the request
| 0x03 | Invalid data value |  | Related to the request
| 0x04 | Service fault |  | The communication module of slave cannot take out the data fault during processing
7 | Modbus Communication Indicators
| Communication type | Response speed |  | Remark
| modbusTCP | ≤10ms |  | Limit 4 clients (high-voltage direct current limit 5 clients)
| modbusRTU（9600 baud rate) | ≤300ms |  | Determined by the number of request registers and baud rate, this indicator is for scenarios with 9600 baud rate and 120 request registers. It is recommended to refer to the processing time of 50ms per frame of the program and the message transmission time at baud rate

## Contents
Module ID | First level directory | Second level directory | BCS1250K-C-HUD(V1.0) | Description
1 | Input register definition | Device information | √
2 | Holding register definition | System operation information | √
|  | Unit information | √
|  | System setting information | √
|  | Battery operation information | √
|  | Battery setting information | √
3 | Alarm information | Alarm word 1-7 | √

## 1-Input register definition
|  |  | ID | Function name |  |  | Function description
|  | Return to contents | 1 | Input register definition
Point table definition
Point type | Function code | Address | Name | Data type | Bit sequence | Status definition | Number of registers | Precision | Unit | Read/Write attribute | Effective mode | Remarks (noun explanation, special treatment, etc.) | BCS1250K-C-HUD(V1.0)
[13 empty] | Enable | Min. value | Max. value | Default value | Option range | Permission level | Alarm level | Remarks
Device information | 0x04 | 4800 | Device model | String | / | / | 10 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4810 |  | / | / | / | 10 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4820 | HMI software version | String | / | / | 5 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4825 | Device serial number | String | / | / | 10 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4835 |  | / | / | / | 15 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4850 |  | UINT16 | / | 20-三相储能变流器 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 厂家 | / | /
| 0x04 | 4851 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4852 |  | UINT16 | / | 2-三相集中式储能变流器协议 3-三相模块化储能变流器协议 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4853 |  | String | / | / | 5 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x04 | 4858 | Manufacturer information | String | / | / | 15 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4873 | 设备串号 | / | / | / | 2 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4875 | Device serial number | String | / | / | 10 | / | / | RO | / | / | √ | / | / | / | / | 客户 | / | /
| 0x04 | 4885 | Unit 1 control software 1 version | String | / | / | 5 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4890 | Unit 1 control software 2 version | String | / | / | 5 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4895 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4900 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4905 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4910 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4915 | Unit 1 hardware 1 version | String | / | / | 5 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4920 | Unit 2 control software 1 version | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4925 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4930 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4935 | Unit 2 control software 1 version | String | / | / | 5 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4940 | Unit 2 control software 2 version | String | / | / | 5 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4945 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4950 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4955 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4960 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4965 | Unit 2 hardware 1 version | String | / | / | 5 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 4970 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4975 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4980 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 4985 |  | / | / | / | 50 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 5035 |  | / | / | / | 50 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 5085 |  | / | / | / | 50 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 5135 |  | / | / | / | 50 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 5185 | Rated power | UINT16 | / | / | 1 | 1 | kW | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x04 | 5186 |  | UINT16 | / | / | 1 | 1 | kVA | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 5187 |  | UINT16 | / | / | 1 | 1 | kW | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 5188 |  | UINT16 | / | / | 1 | 1 | kvar | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 5189 |  | UINT16 | / | / | 1 | 0.01 | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 5190 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x04 | 5195 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5200 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5205 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5210 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5215 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5220 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5225 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5230 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5235 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5240 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5245 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5250 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5255 |  | String | / | / | 5 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5260 |  | / | / | / | 30 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5290 |  | / | / | / | 30 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5320 |  | / | / | / | 30 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x04 | 5350 |  | / | / | / | 30 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /

## 2-Holding register definition
|  |  | ID | Function name |  | Function description
|  | Return to contents | 2 | Holding register definition
Point table definition
Point type | Function code | Address | Name | Data type | Bit sequence | Status definition | Number of registers | Precision | Unit | Read/Write attribute | Effective mode | Remarks (noun explanation, special treatment, etc.) | BCS1250K-C-HUD(V1.0)
[13 empty] | Enable | Min. value | Max. value | Default value | Option range | Permission level | Alarm level | Remarks
System operation information | 0x03 | 7000 | Operating status | ENUM | / | 0-Off 1-Stabdby 2-Fault 3-Charge 4-Discharge 5-Chg. derate 6-Disch. derate | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7001 | System apparent power | UINT32 | / | / | 2 | 1 | VA | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7003 | System active power | INT32 | / | / | 2 | 1 | W | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7005 | System reactive power | INT32 | / | / | 2 | 1 | var | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7007 |  | / | / | / | 3 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x03 | 7010 |  | INT16 | / | / | 1 | 0.01 | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7011 |  | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | 系统输出U相电流
| 0x03 | 7012 |  | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | 系统输出V相电流
| 0x03 | 7013 |  | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | 系统输出W相电流
| 0x03 | 7014 | Day charged energy | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7016 | Day discharged energy | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7018 | Total charged energy | UINT32 | / | / | 2 | 1 | kWh | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7020 | Total discharged energy | UINT32 | / | / | 2 | 1 | kWh | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7022 | AC charge power | INT16 | / | / | 1 | 1 | kW | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7023 | AC side inductive reactive power | UINT16 | / | / | 1 | 1 | kvar | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7024 | AC discharge power | INT16 | / | / | 1 | 1 | kW | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7025 | AC side capacitive reactive power | UINT16 | / | / | 1 | 1 | kvar | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7026 | Max. capacitive reactive power | UINT16 | / | / | 1 | 1 | kvar | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7027 | Max. inductive reactive power | UINT16 | / | / | 1 | 1 | kvar | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7028 | Max. charge power | UINT16 | / | / | 1 | 1 | kW | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7029 | Max. discharge power | UINT16 | / | / | 1 | 1 | kW | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7030 | AC switch status | ENUM | / | 0-Off；1-On | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7031 | DC switch status | ENUM | / | 0-Off；1-On | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7032 | Remote input/exit status | ENUM | / | 0-Exit；1-Input | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7033 | Charging limit current real-time value | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7034 | Discharge limit current real-time value | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7035 | power factor | INT16 | / | / | 1 | 0.001 | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7036 |  | UINT16 | / | / | 1 | / | V | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7037 |  | UINT16 | / | / | 1 | / | Hz | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7038 | Grid-tied/off-grid status | ENUM | / | 0-Grid-tied; 1-Off-grid; 2-VSG; 3-Grid-forming; 4-Auto grid-tied and off-grid; | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7039 | System alarm 1 | Bitfield16 | / | Please refer to Table 3-Alarm information for a detailed definition of alarm information | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7040 | System alarm 2 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7041 | System alarm 3 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7042 | System alarm 4 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7043 | System alarm 5 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7044 | System alarm 6 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7045 | System alarm 7 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7046 | System alarm 8 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7047 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7048 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7049 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7050 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7051 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7052 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7053 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7054 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7055 | System grid UV line voltage/ System grid AB line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7056 | System grid VW line voltage/ System grid BC line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7057 | System grid WU line voltage/ System grid CA line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7058 | System DC power | INT32 | / | / | 2 | 1 | W | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7060 |  | / | / | / | 140 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
Unit information | 0x03 | 7200 | Unit 1 alarm 1 | Bitfield16 | / | Please refer to Table 3-Alarm information for a detailed definition of alarm information | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7201 | Unit 1 alarm 2 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7202 | Unit 1 alarm 3 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7203 | Unit 1 alarm 4 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7204 | Unit 1 alarm 5 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7205 | Unit 1 alarm 6 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7206 | Unit 1 alarm 7 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7207 | Unit 1 alarm 8 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7208 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7209 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7210 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7211 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7212 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7213 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7214 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7215 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7216 | Unit 1 grid UV line voltage/ Unit 1 grid AB line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | Unit 1 Grid UV line voltage
| 0x03 | 7217 | Unit 1 grid VW line voltage/ Unit 1 grid BC line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | Unit 1 Grid VW line voltage
| 0x03 | 7218 | Unit 1 grid WU line voltage/ Unit 1 grid CA line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | Unit 1 Grid WU line voltage
| 0x03 | 7219 | Unit 1 output U current/ Unit 1 output A current | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | Unit 1 Output U current
| 0x03 | 7220 | Unit 1 output V current/ Unit 1 output B current | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | Unit 1 Output V current
| 0x03 | 7221 | Unit 1 output W current/ Unit 1 output C current | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | Unit 1 Output W current
| 0x03 | 7222 | Unit 1 apparent power | UINT32 | / | / | 2 | 1 | VA | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7224 | Unit 1 active power | INT32 | / | / | 2 | 1 | W | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7226 | Unit 1 reactive power | INT32 | / | / | 2 | 1 | var | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7228 |  | INT16 | / | / | 1 | 0.01 | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7229 | Unit 1 DC voltage | INT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7230 | Unit 1 DC current | INT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7231 | Unit 1 DC power | INT32 | / | / | 2 | 1 | W | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7233 | Unit 1 Grid frequency | UINT16 | / | / | 1 | 0.01 | Hz | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7234 | Unit 1 internal temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7235 | Unit 1 phase U IGBT temperature/ Unit 1 phase A IGBT temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | Unit 1 Output U current
| 0x03 | 7236 | Unit 1 phase V IGBT temperature/ Unit 1 phase B IGBT temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | Unit 1 Output V current
| 0x03 | 7237 | Unit 1 phase W IGBT temperature/ Unit 1 phase C IGBT temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | Unit 1 Output W current
| 0x03 | 7238 | Unit 1 grid-tied/off-grid status | ENUM | / | 0-Grid-tied; 1-Off-grid; 2-VSG; 3-Grid-forming; 4-Auto grid-tied and off-grid; | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7239 | Unit 1 available power | UINT16 | / | / | 1 | 0.1 | kVA | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7240 | Unit 1 total load ratio | UINT16 | / | / | 1 | 0.1 | % | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7241 |  | UINT16 | / | / | 1 | 0.1 | mA | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7242 | Unit 1 insulation impedance | UINT16 | / | / | 1 | 0.1 | kΩ | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7243 | Unit 1 charge limit current real-time value | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7244 | Unit 1 discharge limit current real-time value | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7245 |  | ENUM | / | 0-关机；1-开机；2-交流连接待机；3-交流断开待机 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7246 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7248 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7250 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7252 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7254 | Unit 1 max. capacitive reactive power | UINT16 | / | / | 1 | 1 | kvar | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7255 | Unit 1 max. inductive reactive power | UINT16 | / | / | 1 | 1 | kvar | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7256 | Unit 1 max. charge power | UINT16 | / | / | 1 | 1 | kW | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7257 | Unit 1 max. discharge power | UINT16 | / | / | 1 | 1 | kW | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7258 | Unit 1 power factor | INT16 | / | / | 1 | 0.001 | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7259 | Unit 1 operating status | ENUM | / | See option range | 1 | / | / | RO | / | / | √ | / | / | / | 0-Off 1-Stabdby 2-Fault 3-Charge 4-Discharge 5-Chg. derate 6-Disch. Derate | Customer | / | /
| 0x03 | 7260 | Unit 1 bus voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | 运维 | / | /
| 0x03 | 7261 |  | INT16 | / | / | 1 | 1 | kW | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7262 |  | INT16 | / | / | 1 | 1 | kvar | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7263 | Unit 1 inverter UV line voltage/ Unit 1 inverter AB line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7264 | Unit 1 inverter VW line voltage/ Unit 1 inverter BC line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7265 | Unit 1 inverter WU line voltage/ Unit 1 inverter CA line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7266 | Unit 1 AC relay status | ENUM | / | 0-断开；1-吸合 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7267 | Unit 1 DC relay status | ENUM | / | 0-断开；1-吸合 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7268 |  | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7269 | Unit 1 Bus capacitor temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7270 | Unit 1 AC/DC copper bar temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7271 |  | / | / | / | 29 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x03 | 7300 | Unit 2 alarm 1 | Bitfield16 | / | Please refer to Table 3-Alarm information for a detailed definition of alarm information | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7301 | Unit 2 alarm 2 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7302 | Unit 2 alarm 3 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7303 | Unit 2 alarm 4 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7304 | Unit 2 alarm 5 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7305 | Unit 2 alarm 6 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7306 | Unit 2 alarm 7 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7307 | Unit 2 alarm 8 | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7308 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7309 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | √ | / | / | / | / | 厂家 | / | /
| 0x03 | 7310 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7311 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7312 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7313 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7314 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7315 |  | Bitfield16 | / |  | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7316 | Unit 2 grid UV line voltage/ Unit 2 grid AB line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | Unit 2 Grid UV line voltage
| 0x03 | 7317 | Unit 2 grid VW line voltage/ Unit 2 grid BC line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | Unit 2 Grid VW line voltage
| 0x03 | 7318 | Unit 2 grid WU line voltage/ Unit 2 grid CA line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | Unit 2 Grid WU line voltage
| 0x03 | 7319 | Unit 2 output U current/ Unit 2 output A current | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | Unit 2 Output U current
| 0x03 | 7320 | Unit 2 output V current/ Unit 2 output B current | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | Unit 2 Output V current
| 0x03 | 7321 | Unit 2 output W current/ Unit 2 output C current | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | Unit 2 Output W current
| 0x03 | 7322 | Unit 2 apparent power | UINT32 | / | / | 2 | 1 | VA | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7324 | Unit 2 active power | INT32 | / | / | 2 | 1 | W | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7326 | Unit 2 reactive power | INT32 | / | / | 2 | 1 | var | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7328 |  | INT16 | / | / | 1 | 0.01 | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7329 | Unit 2 DC voltage | INT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7330 | Unit 2 DC current | INT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7331 | Unit 2 DC power | INT32 | / | / | 2 | 1 | W | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7333 | Unit 2 Grid frequency | UINT16 | / | / | 1 | 0.01 | Hz | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7334 | Unit 2 internal temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7335 | Unit 2 phase U IGBT temperature/ Unit 2 phase A IGBT temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | Unit 2 U IGBT temperature
| 0x03 | 7336 | Unit 2 phase V IGBT temperature/ Unit 2 phase B IGBT temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | Unit 2 V IGBT temperature
| 0x03 | 7337 | Unit 2 phase W IGBT temperature/ Unit 2 phase C IGBT temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | Unit 2 W IGBT temperature
| 0x03 | 7338 | Unit 2 grid-tied/off-grid status | ENUM | / | 0-Grid-tied; 1-Off-grid; 2-VSG; 3-Grid-forming; 4-Auto grid-tied and off-grid; | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | /
| 0x03 | 7339 | Unit 2 available power | UINT16 | / | / | 1 | 0.1 | kVA | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7340 | Unit 2 total load ratio | UINT16 | / | / | 1 | 0.1 | % | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7341 |  | UINT16 | / | / | 1 | 0.1 | mA | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7342 | Unit 2 insulation impedance | UINT16 | / | / | 1 | 0.1 | kΩ | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7343 | Unit 2 charge limit current real-time value | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7344 | Unit 2 discharge limit current real-time value | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7345 |  | ENUM | / | 0-关机；1-开机；2-交流连接待机；3-交流断开待机 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7346 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7348 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7350 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7352 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7354 | Unit 2 max. capacitive reactive power | UINT16 | / | / | 1 | 1 | kvar | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7355 | Unit 2 max. inductive reactive power | UINT16 | / | / | 1 | 1 | kvar | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7356 | Unit 2 max. charge power | UINT16 | / | / | 1 | 1 | kW | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7357 | Unit 2 max. discharge power | UINT16 | / | / | 1 | 1 | kW | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7358 | Unit 2 power factor | INT16 | / | / | 1 | 0.001 | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7359 | Unit 2 operating status | ENUM | / | See option range | 1 | / | / | RO | / | / | √ | / | / | / | 0-Off 1-Stabdby 2-Fault 3-Charge 4-Discharge 5-Chg. derate 6-Disch. Derate | Customer | / | /
| 0x03 | 7360 | Unit 2 bus voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | 运维 | / | /
| 0x03 | 7361 |  | INT16 | / | / | 1 | 1 | kW | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7362 |  | INT16 | / | / | 1 | 1 | kvar | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7363 | Unit 2 inverter UV line voltage/ Unit 2 inverter AB line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7364 | Unit 2 inverter VW line voltage/ Unit 2 inverter BC line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7365 | Unit 2 inverter WU line voltage/ Unit 2 inverter CA line voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7366 | Unit 2 AC relay status | ENUM | / | 0-断开；1-吸合 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7367 | Unit 2 DC relay status | ENUM | / | 0-断开；1-吸合 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 运维 | / | /
| 0x03 | 7368 |  | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 7369 | Unit 2 Bus capacitor temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7370 | Unit 2 AC/DC copper bar temperature | INT16 | / | / | 1 | 0.1 | ℃ | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 7371 |  | / | / | / | 29 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x03 | 7400 |  | / | / | / | 100 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x03 | 7500 |  | / | / | / | 100 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x03 | 7600 |  | / | / | / | 100 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x03 | 7700 |  | / | / | / | 100 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
System setting information | 0x06 | 7800 | On/Off | ENUM | / | 0-Off; 1-On | 1 | / | / | RW | Effective when online | / | √ | / | / | 0 | / | Customer | / | /
| 0x06 | 7801 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 关机生效 | / | ○ | / | / | 0 | / | 客户 | / | /
| 0x06 | 7802 | Grid rated frequency | ENUM | / | 0-50Hz；1-60Hz | 1 | / | Hz | RW | 关机生效 | / | √ | / | / | 根据并网标准 | / | 厂家 | / | 当前版本仅支持50Hz
| 0x06 | 7803 | High/Low voltage ride-through mode | ENUM | / | 0-Disable; 1-Enable(reactive power support mode) 2-Enable(zero current mode) 3-Enable(active power priority mode) | 1 | / | / | RW | Effective when online | / | √ | / | / | / | 0-3 | Customer | / | /
| 0x06 | 7804 | Active island | ENUM | / | 0-Disable; 1-Enable | 1 | / | / | RW | Effective when online | / | √ | / | / | 0 | / | Customer | / | /
| 0x06 | 7805 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | 0 | / | 客户 | / | /
| 0x06 | 7806 |  | ENUM | / | 0-恒功率；1-恒流 | 1 | / | / | RW | 在线生效 | / | √ | / | / | 0 | / | 厂家 | / | /
| 0x06 | 7807 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 7808 | Reactive power operation mode | ENUM | / | 0-Constant reactive power; 1-Constant power factor | 1 | / | / | RW | Effective after shutdown | / | √ | 0 | 1 | 0 | / | Customer | / | /
| 0x06 | 7809 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 7810 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7811 | Active power | INT16 | / | / | 1 | 1 | kW | RW | Effective when online | / | √ | / | / | 0 | / | Customer | / | /
| 0x06 | 7812 | Reactive power | INT16 | / | / | 1 | 1 | kvar | RW | Effective when online | / | √ | / | / | 0 | / | Customer | / | /
| 0x06 | 7813 |  | INT16 | / | / | 1 | 0.01 | / | RW | 在线生效 | / | ○ | -1 | 1 | 1 | / | 客户 | / | /
| 0x06 | 7814 |  | INT16 | / | / | 1 | 0.1 | A | RW | 在线生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x10 | 7815 | Power prestart rate | UINT32 | / | power change rate during operation process | 2 | 0.01 | %/s | RW | Effective when online | / | √ | 0.01 | 50000 | / | / | 厂家 | / | /
| 0x10 | 7817 | On/Off prestart rate | UINT32 | / | power change rate during power on/off process | 2 | 0.01 | %/s | RW | Effective when online | / | √ | 0.01 | 50000 | / | / | Customer | / | /
| 0x06 | 7819 |  | UINT16 | / | / | 1 | / | / | RW | 关机生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 7820 |  | ENUM | / | 0-不恢复；1-恢复，仅在“电网异常自恢复”禁止状态，且电网异常恢复后有效。 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 7821 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 关机生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 7822 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 7823 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 7824 | Fault recovery time | UINT16 | / | / | 1 | 1 | s | RW | Effective when online | / | √ | 1 | 600 | / | / | Customer | / | /
| 0x06 | 7825 |  | UINT16 | / | [0.0,1500.0] | 1 | 0.1 | V | RW | 在线生效 | / | √ | / | / | 1200 | / | 厂家 | / | /
| 0x06 | 7826 |  | UINT16 | / | [1,3600] | 1 | 1 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 7827 |  | UINT16 | / | [270,1000] | 1 | 1 | V | RW | 在线生效 | / | ○ | / | / | 690 | / | 客户 | / | /
| 0x06 | 7828 | Standby control method | ENUM | / | See option range | 1 | / | / | RW | Effective after shutdown | / | √ | 0 | 3 | 0 | 0-Pulse off； 1-Running； 2-OFF； 3-AC disconnecting | Customer | / | /
| 0x06 | 7829 |  | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | ○ | / | / | 50 | / | 客户 | / | /
| 0x06 | 7830 |  | UINT16 | / | [0.1,30.0] | 1 | 0.1 | s | RW | 在线生效 | / | ○ | / | / | 5.7 | / | 客户 | / | /
| 0x06 | 7831 |  | UINT16 | / | [0,10000] | 1 | 1 | / | RW | 在线生效 | / | ○ | / | / | 1050 | / | 客户 | / | /
| 0x06 | 7832 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 7833 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 7834 | EMS charge limit current | UINT16 | / | / | 1 | 0.1 | A | RW | Effective when online | / | √ | / | / | 0 | / | Customer | / | /
| 0x06 | 7835 | EMS discharge limit current | UINT16 | / | / | 1 | 0.1 | A | RW | Effective when online | / | √ | / | / | 0 | / | Customer | / | /
| 0x06 | 7836 | power factor | INT16 | / | / | 1 | 0.001 | / | RW | Effective when online | / | √ | / | / | 1 | / | Customer | / | /
| 0x06 | 7837 | Remote communication fault power reduction | UINT16 | / | / | 1 | 1 | s | RW | Effective when online | / | √ | 1 | 600 | 300 | / | Customer | / | /
| 0x06 | 7838 |  | UINT16 | / | / | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | [0-65535] | 客户 | / | /
| 0x06 | 7839 |  | / | / | / | 2 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7841 | Fault reset | ENUM | / | 0-Invalid；1-Enable | 1 | / | / | RW | Effective when online | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 7842 | Harmonic compensation | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 7843 | Reactive power priority | ENUM | / | 0-Disable; 1-Enable | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | 0 | / | Customer | / | /
| 0x06 | 7844 |  | ENUM | / | 0-GFDI；1-绝缘阻抗检测 | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 7845 | Insulation impedance detection | ENUM | / | 0-Disable;1-Alarm;2-Protect | 1 | / | / | RW | Effective when online | / | √ | / | / | 2 | / | Customer | / | /
| 0x06 | 7846 |  | UINT16 | / | [0.0,视在功率] | 1 | 0.1 | kW | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 7847 | Apparent power | UINT16 | / | / | 1 | 1 | kVA | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 7848 | Standard type | ENUM | / | 0-自定义； 1-中国； 2-美国； 3-美国加州； 4-德国； 5-澳洲； 6-新西兰； 7-英国； 8-泰国PEA； 9-泰国MEA； 10-意大利； 11-加拿大； 12-法国VFR； 13-法国SEI； 14-法国CRAE； 15-法国VDE； 16-荷兰； 17-西班牙； 18-EN50438； 19-印度； 20-韩国； 22-墨西哥； 23-日本； 24-越南； 25-俄罗斯； 26-乌克兰； 27-台湾； 28-EN50549-2； 29-波兰TypeD； 30-IEC61727； 31-北美； 32-德国4110； 33-德国4105； 34-EN50549-1； 35-巴西； 36-智利； 37-CEI0-21； 38-奥地利； 39-CEI0-16； 40-G99-TypeB； 41-G99-TypeC； 42-G99-TypeD； 43-瑞典； 44-波兰TypeB； 45-波兰TypeC； 46-Australia A； 47-Australia B； 48-Australia C； | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x10 | 7850 | System time | MLB | / | The registers 7850-7855 must be written all at once, otherwise the setting is invalid.Example: If the system time is set to 14:15:30 on January 5, 2020, then registers 7850-7855 should be written to 0x07E4, 0x0001, 0x0005, 0x000E, 0x000F, and 0x001E all at once | 6 | 1 | / | RW | Effective when online | / | √ | / | / | / | / | Customer | / | /
| / | / | System time-year | UINT16 | / | / | / | / | / | RW | / | / | √ | 2000 | 2099 | / | / | Customer | / | /
| / | / | System time-month | UINT16 | / | / | / | / | / | RW | / | / | √ | / | / | / | / | Customer | / | /
| / | / | System time-day | UINT16 | / | / | / | / | / | RW | / | / | √ | 1 | 31 | / | / | Customer | / | /
| / | / | System time-hour | UINT16 | / | / | / | / | / | RW | / | / | √ | 0 | 23 | / | / | Customer | / | /
| / | / | System time-minute | UINT16 | / | / | / | / | / | RW | / | / | √ | 0 | 59 | / | / | Customer | / | /
| / | / | System time-second | UINT16 | / | / | / | / | / | RW | / | / | √ | 0 | 59 | / | / | Customer | / | /
| 0x06 | 7856 | DC parallel mode | ENUM | / | 0-DC independent; 1-DC parallel | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 7857 |  | / | / | / | 7 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7864 |  | UINT16 | / | 寄存器7864-7896必须一次性写入，否则设置无效。 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7865 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7866 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7867 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7868 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7869 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7870 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7871 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7872 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7873 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7874 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7875 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7876 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7877 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7878 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7879 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7880 |  | UINT16 | / | 高字节-小时；低字节-分钟 | 1 | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7881 |  | INT16 | / | / | 1 | 1 | kW | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7882 |  | INT16 | / | / | 1 | 1 | kvar | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7883 |  | INT16 | / | / | 1 | 1 | kW | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7884 |  | INT16 | / | / | 1 | 1 | kvar | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7885 |  | INT16 | / | / | 1 | 1 | kW | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7886 |  | INT16 | / | / | 1 | 1 | kvar | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7887 |  | INT16 | / | / | 1 | 1 | kW | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7888 |  | INT16 | / | / | 1 | 1 | kvar | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7889 |  | INT16 | / | / | 1 | 1 | kW | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7890 |  | INT16 | / | / | 1 | 1 | kvar | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7891 |  | INT16 | / | / | 1 | 1 | kW | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7892 |  | INT16 | / | / | 1 | 1 | kvar | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7893 |  | INT16 | / | / | 1 | 1 | kW | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7894 |  | INT16 | / | / | 1 | 1 | kvar | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7895 |  | INT16 | / | / | 1 | 1 | kW | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7896 |  | INT16 | / | / | 1 | 1 | kvar | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7900 | Grid-tied/Off-grid mode | ENUM | / | 0-Grid-tied; 1-Off-grid; 2-VSG; 3-Grid-forming; 4-Auto grid-tied and off-grid; | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | 0 | 0-4 | Customer | / | /
| 0x06 | 7901 |  | UINT16 | / | [1,65535] | 1 | / | / | RW | 关机生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7902 |  | ENUM | / | 0-单机；1-并机 | 1 | / | / | RW | 关机生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7903 |  | / | / | / | 36 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 7939 |  | UINT16 | / | / | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 7940 |  | UINT16 | / | / | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 7941 |  | UINT16 | / | / | 1 | 1 | V | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 7942 |  | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 7943 |  | / | / | / | 57 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8000 | Time zone setting | ENUM | / | 1 - (UTC-12:00) International Date Line West ; 2 - (UTC-11:00) Coordinated Universal Time-11 ; 3 - UTC-10:00 ; 4 - (UTC-10:00) Hawaii ; 5 - UTC-09:00 ; 6 - (UTC-09:00) Alaska ; 7 - UTC-08:00 ; 8 - (UTC-08:00) Pacific Time (US and Canada) ; 9 - UTC-07:00 ; 10 - (UTC-07:00) Mountain Time (US and Canada) ; 11 - UTC-06:00 ; 12 - (UTC-06:00) Central Time (US and Canada) ; 13 - UTC-05:00 ; 14 - (UTC-05:00) Eastern Time (US and Canada) ; 15 - UTC-04:00 ; 16 - UTC-03:00 ; 17 - (UTC-03:00) Brasilia ; 18 - UTC-02:00 ; 19 - UTC-01:00 ; 20 - UTC-00:00 ; 21 - (UTC+00:00) Dublin, Edinburgh, Lisbon, London ; 22 - UTC+01:00 ; 23 - UTC+02:00 ; 24 - UTC+03:00 ; 25 - UTC+04:00 ; 26 - (UTC+04:00) Abu Dhabi, Muscat ; 27 - UTC+05:00 ; 28 - (UTC+05:00) Islamabad, Karachi ; 29 - UTC+06:00 ; 30 - (UTC+06:00) Astana, Dhaka ; 31 - UTC+07:00 ; 32 - (UTC+08:00) Beijing, Chongqing, Hong Kong, Urumqi ; 33 - UTC+09:00 ; 34 - (UTC+09:00) Osaka, Sapporo, Tokyo ; 35 - UTC+10:00 ; 36 - (UTC+10:00) Sydney, Melbourne ; 37 - UTC+11:00 ; 38 - UTC+12:00 ; 39 - UTC+13:00 ; 40 - UTC+14:00 | 1 | / | / | RW | Effective when online | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 8001 | Automatic daylight saving time adjustment | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x10 | 8002 | NTP time sync cycle | UINT32 | / | [10,86400] | 2 | 1 | s | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x10 | 8004 | NTP server IP address | MLB | / | 寄存器8004-8007必须一次性写入，否则设置无效。例：设置NTP服务器IP地址192.168.0.1,那么寄存器8004-8007应一次性写入0x00C0 0x00A8 0x0000 0x0001 | 4 | 1 | / | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| / | / | NTP server IP address 1 | UINT16 | / | [0,255] | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / | NTP server IP address 2 | UINT16 | / | [0,255] | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / | NTP server IP address 3 | UINT16 | / | [0,255] | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / | NTP server IP address 4 | UINT16 | / | [1,254] | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8008 |  | / | / | / | 12 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x10 | 8020 |  | MLB | / | 网口1和网口2不能为同一IP地址。寄存器8020-8043必须一次性写入，否则设置无效。例：设置网口1IP地址192.168.1.10，网口1掩码255.255.255.0，网口1网关192.168.1.1，网口2IP地址192.168.1.11，网口2掩码255.255.255.0，网口2网关192.168.1.1，那么寄存器8020-8043应一次性写入0x00C0 0x00A8 0x0001 0x000A 0x00FF 0x00FF 0x00FF 0x0000 0x00C0 0x00A8 0x0001 0x0001 0x00C0 0x00A8 0x0001 0x000B 0x00FF 0x00FF 0x00FF 0x0000 0x00C0 0x00A8 0x0001 0x0001 | 24 | 1 | / | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8044 |  | / | / | / | 119 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x10 | 8163 | Active power prestart rate | UINT32 | / | / | 2 | 0.01 | %/s | RW | Effective when online | / | √ | 0 | 50000 | 100 | / | Customer | / | /
| 0x06 | 8165 |  | ENUM | / | 0-常开；1-常闭 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x10 | 8166 | Speed change point prestart rate | UINT32 | / | / | 2 | 0.01 | %/s | RW | 在线生效 | / | √ | 0.01 | 50000 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 8168 | Power prestart speed change point | UINT16 | / | / | 1 | 0.1 | % | RW | 在线生效 | / | √ | 80 | 100 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 8169 | Reactive power prestart rate | UINT32 | / | / | 2 | 0.01 | %/s | RW | Effective when online | / | √ | 0 | 50000 | 100 | / | Customer | / | /
| 0x06 | 8171 | Standby mode response time | UINT16 | / | [0.01,300.00] | 1 | 0.01 | s | RW | Effective when online | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 8172 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8173 | BMS communication function | ENUM | / | 0-Disable；1-Enable | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 8174 | BMS dry contact | ENUM | / | 0-Normally open；1-Normally closed | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 8175 | BMS communication mode | ENUM | / | 0-RS485；1-CAN | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | / | / | Customer | / | /
|  | 8176 | BMS CAN protocol type | ENUM | / | 0-Standard； 1-PN； 2-CATL； 3-CATL3.3； 4-CATL3.4； 5-CATL3.5； 6-Gotion； 7-CRRC； 8-CATL3.9； 9-BMSer； 10-CATL4.9； 11-GaoteV1.3; 12-Industry standard; 13-CRRC 0826; 14-Unstd. | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 8177 | BMS RS485 protocol type | ENUM | / | 0-Stabdard；1-Gotion；2-BYD；3-Hyper Strong V1.5；4-Industry standard；5-Unstd. | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 8178 | BMS CAN communication baud rate | ENUM | / | 0-250kbps；1-500kbps；2-1Mbps | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 8179 | BMS 485 baud rate | ENUM | / | 0-9600kbps；1-19200kbps | 1 | / | / | RW | Effective after shutdown | s | √ | / | / | / | / | Customer | / | /
| 0x06 | 8180 | Remote communication abnormal detection time T1 | UINT16 | / | / | 1 | 1 | s | RW | 在线生效 | / | ○ | 1 | 600 | 30s |  | 运维 |  | /
| 0x06 | 8181 | Remote communication abnormal detection time T2 | UINT16 | / | / | 1 | 1 | s | RW | 在线生效 | / | ○ | 1 | 600 | 3s |  | 运维 |  | /
| 0x06 | 8182 | Remote communication abnormal detection time T3 | UINT16 | / | / | 1 | 1 | s | RW | 在线生效 | / | ○ | 1 | 600 | 10s |  | 运维 |  | /
| 0x06 | 8183 | Remote communication abnormal detection time T4 | UINT16 | / | / | 1 | 1 | s | RW | 在线生效 | / | ○ | 1 | 600 | 30s |  | 运维 |  | /
| 0x10 | 8184 | SrvrAct register | UINT32 | / | / | 2 | / | / | RO | / | / | ○ | / | / | / |  | 运维 |  | /
| 0x10 | 8186 | ClntAct register | UINT32 | / | / | 2 | / | / | RW | 在线生效 | / | ○ | / | / | / |  | 运维 |  | /
| 0x06 | 8188 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8189 | Communication abnormal response mode | ENUM | / | 0-保护；1-待机 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8190 | Communication abnormal detection function | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | 0 | / | 运维 | / | /
| 0x06 | 8191 |  | UINT16 | / | / | 1 | / | / | RW | 在线生效 | 闪断次数 | √ | 2 | 20 | 2 | / | 运维 | / | /
| 0x06 | 8192 |  | UINT16 | / | / | 1 | 1 | s | RW | 在线生效 | / | √ | 1 | 600 | 3 | / | 运维 | / | /
| 0x06 | 8193 |  | UINT16 | / | / | 1 | 1 | ms | RW | 在线生效 | 窗口时间 | √ | 1 | 3000 | 3000 | / | 运维 | / | /
| 0x10 | 8194 | Heartbeat write to register | UINT32 | / | / | 2 | 1 | / | RW | Effective when online | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 8196 |  | / | / | / | 4 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
Battery operation information | 0x03 | 8200 | BMS system status | ENUM | / | 0-Initial status；1-Normal status；2-Charge disabled；3-Discharge disabled；4-Alarm；5-Fault；6-Standby | 1 | / | / | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8201 | Battery pack total voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8202 | Battery pack total current | INT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8203 | Battery pack SOC | UINT16 | / | / | 1 | 0.1 | % | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8204 | Battery pack SOH | UINT16 | / | / | 1 | 0.1 | % | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8205 | Charge limit current | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8206 | Discharge limit current | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8207 | Charge limit voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8208 | Discharge limit voltage | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8209 | Charge available energy | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8211 | Discharge available energy | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | √ | / | / | / | / | Customer | / | /
| 0x03 | 8213 |  | / | / | / | 12 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x03 | 8225 |  | ENUM | / | 0-初始状态；1-正常状态；2-禁充；3-禁放；4-告警；5-故障；6-待机 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8226 |  | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8227 |  | INT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8228 |  | UINT16 | / | / | 1 | 0.1 | % | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8229 |  | UINT16 | / | / | 1 | 0.1 | % | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8230 |  | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8231 |  | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8232 |  | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8233 |  | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8234 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8236 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8238 |  | / | / | / | 12 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8250 |  | ENUM | / | 0-初始状态；1-正常状态；2-禁充；3-禁放；4-告警；5-故障；6-待机 | 1 | / | / | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8251 |  | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8252 |  | INT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8253 |  | UINT16 | / | / | 1 | 0.1 | % | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8254 |  | UINT16 | / | / | 1 | 0.1 | % | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8255 |  | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8256 |  | UINT16 | / | / | 1 | 0.1 | A | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8257 |  | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8258 |  | UINT16 | / | / | 1 | 0.1 | V | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8259 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8261 |  | UINT32 | / | / | 2 | 0.1 | kWh | RO | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8263 |  | / | / | / | 12 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8275 |  | / | / | / | 25 | / | / | / | / | 同单元1 | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8300 |  | / | / | / | 25 | / | / | / | / | 同单元1 | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8325 |  | / | / | / | 25 | / | / | / | / | 同单元1 | ○ | / | / | / | / | 客户 | / | /
| 0x03 | 8350 |  | / | / | / | 25 | / | / | / | / | 同单元1 | ○ | / | / | / | / | 客户 | / | /
Battery setting information | 0x06 | 8380 | Equalized-charge voltage | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | 0 | 1510 | 1510 | / | Customer | / | /
| 0x06 | 8381 | Floating charge voltage | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | / | / | / | / | Customer | / | /
| 0x06 | 8382 |  | UINT16 | / | / | 1 | 1 | min | RW | 关机生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8383 |  | UINT16 | / | / | 1 | 1 | A | RW | 关机生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8384 | Battery overvoltage protection point | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | Battery undervoltage protection point | 1550 | 1520 | / | Customer | / | /
| 0x06 | 8385 | Discharge cutoff voltage | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | 0 | 1550 | 1020 | / | Customer | / | /
| 0x06 | 8386 | Battery undervoltage alarm point | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | Battery undervoltage protection point | 1550 | 1030 | / | Customer | / | /
| 0x06 | 8387 | Battery undervoltage protection point | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | Battery heavy load undervoltage protection point | Battery undervoltage alarm point | 1020 | / | Customer | / | /
| 0x06 | 8388 | Battery heavy load undervoltage protection point | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | 0 | Battery undervoltage protection point | 970 | / | Customer | / | /
| 0x06 | 8389 | Battery overvoltage hysteresis | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | 0 | 100 | 20 | / | Customer | / | /
| 0x06 | 8390 | Battery undervoltage hysteresis | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | 0 | 100 | 25 | / | Customer | / | /
| 0x06 | 8391 | Battery heavy load undervoltage hysteresis | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | 0 | 100 | 25 | / | Customer | / | /
| 0x06 | 8392 |  | UINT16 | / | / | 1 | 1 | min | RW | 关机生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8393 | Discharge cutoff voltage hysteresis | UINT16 | / | / | 1 | 1 | V | RW | Effective after shutdown | / | √ | 0 | 100 | 25 | / | Customer | / | /
| 0x06 | 8394 |  | / | / | / | 6 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8400 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8401 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8402 |  | UINT16 | / | / | 1 | 1 | min | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8403 |  | UINT16 | / | / | 1 | 1 | A | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8404 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8405 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8406 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8407 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8408 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8409 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8410 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8411 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8412 |  | UINT16 | / | / | 1 | 1 | min | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8413 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8414 |  | / | / | / | 6 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8420 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8421 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8422 |  | UINT16 | / | / | 1 | 1 | min | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8423 |  | UINT16 | / | / | 1 | 1 | A | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8424 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8425 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8426 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8427 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8428 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8429 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8430 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8431 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8432 |  | UINT16 | / | / | 1 | 1 | min | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8433 |  | UINT16 | / | / | 1 | 1 | V | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8434 |  | / | / | / | 6 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8440 |  | / | / | / | 20 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8460 |  | / | / | / | 20 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8480 |  | / | / | / | 20 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8500 |  | / | / | / | 20 | / | / | / | / | / | ○ | / | / | / | / | 客户 | / | /
单元设置信息 | 0x06 | 8520 |  | ENUM | / | 0-常开；1-常闭 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8521 | Unit 1 on/off | ENUM | / | 0-关机；1-开机 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8522 |  | INT16 | / | / | 1 | 0.1 | A | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | 当前版本不支持，选项范围待定
| 0x06 | 8523 |  | INT16 | / | / | 1 | 1 | kW | RW | 在线生效 | / | ○ | / | / | 0 | / | 客户 | / | /
| 0x06 | 8524 |  | INT16 | / | / | 1 | 1 | kvar | RW | 在线生效 | / | ○ | / | / | 0 | / | 客户 | / | /
| 0x06 | 8525 | Unit 1 power factor | INT16 | / | / | 1 | 0.001 | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 8526 | Unit 1 EMS charge limit current | UINT16 | / | / | 1 | 0.1 | A | RW | 在线生效 | / | ○ | 0 | 250 | 250 | / | 客户 | / | /
| 0x06 | 8527 | Unit 1 EMS discharge limit current | UINT16 | / | / | 1 | 0.1 | A | RW | 在线生效 | / | ○ | 0 | 250 | 250 | / | 客户 | / | /
| 0x06 | 8528 |  | ENUM | / | 0-常开；1-常闭 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8529 | Unit 1 External emergency stop dry contact | ENUM | / | 0-常开；1-常闭 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 8530 | Unit 1 BMS dry contact | ENUM | / | 0-常开；1-常闭 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 8531 | Unit 1 fault reset | ENUM | / | 0-无效；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8532 | Unit 1 charging current setting at zero DC power | INT16 | / | [-20.0,20.0] | 1 | 0.1 | A | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8533 |  | / | / | / | 87 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8620 |  | ENUM | / | 0-常开；1-常闭 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8621 | Unit 2 on/off | ENUM | / | 0-关机；1-开机 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8622 |  | INT16 | / | / | 1 | 0.1 | A | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8623 |  | INT16 | / | / | 1 | 1 | kW | RW | 在线生效 | / | ○ | / | / | 0 | / | 客户 | / | /
| 0x06 | 8624 |  | INT16 | / | / | 1 | 1 | kvar | RW | 在线生效 | / | ○ | / | / | 0 | / | 客户 | / | /
| 0x06 | 8625 | Unit 2 power factor | INT16 | / | / | 1 | 0.001 | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 8626 | Unit 2 EMS charge limit current | UINT16 | / | / | 1 | 0.1 | A | RW | 在线生效 | / | ○ | 0 | 250 | 250 | / | 客户 | / | /
| 0x06 | 8627 | Unit 2 EMS discharge limit current | UINT16 | / | / | 1 | 0.1 | A | RW | 在线生效 | / | ○ | 0 | 250 | 250 | / | 客户 | / | /
| 0x06 | 8628 |  | ENUM | / | 0-常开；1-常闭 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8629 | Unit 2 external emergency stop dry contact | ENUM | / | 0-常开；1-常闭 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 8630 | Unit 2 BMS dry contact | ENUM | / | 0-常开；1-常闭 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | 1 | / | 客户 | / | /
| 0x06 | 8631 | Unit 2 fault reset | ENUM | / | 0-无效；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8632 | Unit 2 charging current setting at zero DC power | INT16 | / | [-20.0,20.0] | 1 | 0.1 | A | RW | 在线生效 | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8633 |  | / | / | / | 88 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 8720 |  | / | / | / | 100 | / | / | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8820 |  | / | / | / | 100 | / | / | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 8920 |  | / | / | / | 100 | / | / | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 9020 |  | / | / | / | 100 | / | / | RW | / | / | ○ | / | / | / | / | 客户 | / | /
| 0x06 | 9120 |  | / | / | / | 880 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
并网标准 | 0x06 | 10000 |  | / | / | / | 82 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10082 | P-V mode | ENUM | / | 0-关闭；1-线性；2-滞回 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10083 | P-V mode HV1 | UINT16 | / | [0.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10084 | P-V mode HP1 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10085 | P-V mode HV2 | UINT16 | / | [100.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10086 | P-V mode HP2 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10087 | P-V mode HV3 | UINT16 | / | [100.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10088 | P-V mode HP3 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10089 | P-V mode LV1 | UINT16 | / | [0.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10090 | P-V mode LP1 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10091 | P-V mode LV2 | UINT16 | / | [0.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10092 | P-V mode LP2 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10093 | P-V mode LV3 | UINT16 | / | [0.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10094 | P-V mode LP3 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10095 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10096 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10097 | P-V mode power reference | ENUM | / | 0-最大功率百分比；1-可用功率百分比 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x10 | 10098 | P-V mode hysteresis time | UINT32 | / | [0.00,600.00] | 2 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x10 | 10100 | P-V mode response time | UINT32 | / | [0.00,200.00] | 2 | 0.01 | s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10102 |  | / | / | / | 12 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10114 | Q-V mode power lock function | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10115 | Q-V mode power lock entry point | UINT16 | / | [0,20] | 1 | 1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10116 | Q-V mode power lock exit point | UINT16 | / | [0,20] | 1 | 1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10117 | Q-V mode power adjustment coefficient | INT16 | / | [-0.10,0.10] | 1 | 0.01 | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10118 | Q-V mode power priority | ENUM | / | 0-有功优先；1-无功优先；2-Vendor | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10119 | Q-V mode power reference | ENUM | / | 0-最大有功功率百分比； 1-最大无功功率百分比； 2-可用无功功率百分比； 3-视在功率百分比 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10120 | Q-V mode AutoVref enable | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10121 | Q-V mode AutoVref adjustment time | UINT16 | / | [1,5000] | 1 | 1 | s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10122 | Q-V mode starting reactive power | INT16 | / | [-60.0,60.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10123 | Q-V mode voltage dead zone | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10124 | Q-V mode | ENUM | / | 0-关闭；1-线性；2-死区 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10125 | Q-V mode V1 | UINT16 | / | [80.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10126 | Q-V mode Q1 | INT16 | / | [-60.0,60.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10127 | Q-V mode V2 | UINT16 | / | [80.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10128 | Q-V mode Q2 | INT16 | / | [-60.0,60.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10129 | Q-V mode V3 | UINT16 | / | [100.0, 135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10130 | Q-V mode Q3 | INT16 | / | [-60.0,60.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10131 | Q-V mode V4 | UINT16 | / | [100.0, 135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10132 | Q-V mode Q4 | INT16 | / | [-60.0,60.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10133 | Q-V mode V5 | UINT16 | / | [100.0, 135.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10134 | Q-V mode Q5 | INT16 | / | [-60.0,60.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10135 | Q-V mode V6 | UINT16 | / | [100.0, 135.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10136 | Q-V mode Q6 | INT16 | / | [-60.0,60.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10137 | Q-V mode hysteresis | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10138 | Q-V mode Vref | UINT16 | / | [95.0,105.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10139 |  | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x10 | 10140 | Q-V mode response time | UINT32 | / | [0.00,100.00] | 2 | 0.01 | s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10142 |  | UINT16 | / | [0.001,1.000] | 1 | 0.001 | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10143 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10144 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10145 | Watt-Var mode | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10146 | Watt-Var mode P1 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10147 | Watt-Var mode Q1 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10148 | Watt-Var mode P2 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10149 | Watt-Var mode Q2 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10150 | Watt-Var mode P3 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10151 | Watt-Var mode Q3 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10152 | Watt-Var mode P4 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10153 | Watt-Var mode Q4 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10154 | Watt-Var mode P1' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10155 | Watt-Var mode Q1' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10156 | Watt-Var mode P2' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10157 | Watt-Var mode Q2' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10158 | Watt-Var mode P3' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10159 | Watt-Var mode Q3' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10160 | Watt-Var mode P4' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10161 | Watt-Var mode Q4' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10162 | Watt-Var mode P5 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10163 | Watt-Var mode Q5 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10164 | Watt-Var mode P5' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10165 | Watt-Var mode Q5' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10166 | Watt-var mode power priority | ENUM | / | 0-有功优先；1-无功优先 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10167 | Watt-var mode power reference | ENUM | / | 0-最大有功功率百分比； 1-最大无功功率百分比； 2-可用无功功率百分比； 3-视在功率百分比 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x10 | 10168 | Watt-Var mode response time | UINT32 | / | [0.00,200.00] | 2 | 0.01 | s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10170 |  | UINT16 | / | [0,10] | 1 | 1 | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10171 |  | / | / | / | 65 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10236 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10237 |  | / | / | / | 2 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10239 |  | UINT16 | / | / | 1 | 0.01 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10240 |  | UINT16 | / | / | 1 | 0.01 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10241 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10242 |  | INT16 | / | / | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10243 |  | UINT16 | / | / | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x10 | 10244 |  | UINT32 | / | / | 2 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x10 | 10246 |  | UINT32 | / | / | 2 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x10 | 10248 |  | UINT32 | / | / | 2 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10250 |  | / | / | / | 10 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10260 |  | UINT16 | / | / | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10261 |  | UINT16 | / | [0.00,200.00] | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10262 |  | UINT16 | / | [1.00,600.00] | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10263 |  | UINT16 | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10264 | Power-on grid reconnection recovery time | UINT16 | / | [1,10000] | 1 | 1 | s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10265 |  | / | / | / | 15 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10280 | Grid level Ⅰ undervoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 电网II级欠压保护值 | 100 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10281 | Grid level Ⅱ undervoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 电网III级欠压保护值 | 电网I级欠压保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10282 | Grid level Ⅲ undervoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 电网IV级欠压保护值 | 电网II级欠压保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10283 | Grid level Ⅳ undervoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 电网V级欠压保护值 | 电网III级欠压保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10284 | Grid level Ⅴ undervoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 0 | 电网IV级欠压保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10285 | Grid level Ⅰ undervoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 30 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10287 | Grid level Ⅱ undervoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 30 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10289 | Grid level Ⅲ undervoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 30 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10291 | Grid level Ⅳ undervoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 30 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10293 | Grid level Ⅴ undervoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 30 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10295 | Grid level Ⅰ overvoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 100 | 电网II级过压保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10296 | Grid level Ⅱ overvoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 电网I级过压保护值 | 电网III级过压保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10297 | Grid level Ⅲ overvoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 电网II级过压保护值 | 电网IV级过压保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10298 | Grid level Ⅳ overvoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 电网III级过压保护值 | 电网V级过压保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10299 | Grid level Ⅴ overvoltage protection value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 电网IV级过压保护值 | 135 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10300 | Grid level Ⅰ overvoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 100 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10302 | Grid level Ⅱ overvoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 15 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10304 | Grid level Ⅲ overvoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 15 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10306 | Grid level Ⅳ overvoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 1 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10308 | Grid level Ⅴ overvoltage protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 1 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10310 | Grid undervoltage protection recovery value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 电网I级欠压保护值 | 100 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10311 | Grid overvoltage protection recovery value | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | √ | 100 | 电网I级过压保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10312 | Grid level Ⅰ underfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 电网II级欠频保护值 | 65 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10313 | Grid level Ⅱ underfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 电网III级欠频保护值 | 电网I级欠频保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10314 | Grid level Ⅲ underfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 电网IV级欠频保护值 | 电网II级欠频保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10315 | Grid level Ⅳ underfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 电网V级欠频保护值 | 电网III级欠频保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10316 | Grid level Ⅴ underfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 45 | 电网IV级欠频保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10317 | Grid level Ⅰ underfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 7200 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10319 | Grid level Ⅱ underfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 7200 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10321 | Grid level Ⅲ underfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 7200 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10323 | Grid level Ⅳ underfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 5 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10325 | Grid level Ⅴ underfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 5 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10327 | Grid level Ⅰ overfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 45 | 电网II级过频保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10328 | Grid level Ⅱ overfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 电网I级过频保护值 | 电网III级过频保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10329 | Grid level Ⅲ overfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 电网II级过频保护值 | 电网IV级过频保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10330 | Grid level Ⅳ overfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 电网III级过频保护值 | 电网V级过频保护值 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10331 | Grid level Ⅴ overfrequency protection value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 电网IV级过频保护值 | 65 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10332 | Grid level Ⅰ overfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 7200 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10334 | Grid level Ⅱ overfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 7200 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10336 | Grid level Ⅲ overfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 7200 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10338 | Grid level Ⅳ overfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 5 | 根据并网标准设置 | / | 运维 | / | /
| 0x10 | 10340 | Grid level Ⅴ overfrequency protection time | UINT32 | / | / | 2 | 0.001 | s | RW | 关机生效 | / | √ | 0.001 | 5 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10342 | Grid underfrequency protection recovery value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 45 | 65 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10343 | Grid overfrequency protection recovery value | UINT16 | / | / | 1 | 0.01 | Hz | RW | 关机生效 | / | √ | 45 | 65 | 根据并网标准设置 | / | 运维 | / | /
| 0x06 | 10344 | Grid 10-minute overvoltage protection function | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10345 | Grid 10-minute overvoltage protection value | UINT16 | / | [100.0, 135.0] | 1 | 0.1 | % | RW | 关机生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10346 |  | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10347 |  | UINT16 | / | [100.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10348 |  | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10349 |  | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10350 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x10 | 10351 |  | UINT32 | / | [0.01,50000.00] | 2 | 0.01 | %/s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x10 | 10353 |  | / | / | / | 21 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10374 |  | UINT16 | / | [0.00,3.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 10375 |  | UINT16 | / | [0.00,3.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 10376 |  | UINT16 | / | [0.00,3.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 10377 |  | UINT16 | / | [0.00,3.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 10378 |  | UINT16 | / | [0.00,3.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 10379 |  | UINT16 | / | [0.00,3.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 10380 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10381 |  | UINT16 | / | [0.00,10.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10382 |  | UINT16 | / | [0.00,10.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10383 |  | UINT16 | / | [0.00,10.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10384 |  | UINT16 | / | [0.00,10.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10385 |  | UINT16 | / | [0.00,10.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10386 |  | UINT16 | / | [0.00,10.00] | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10387 |  | UINT16 | / | / | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10388 |  | UINT16 | / | / | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10389 |  | UINT16 | / | [0,1000] | 1 | 1 | %/s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10390 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10391 | HVRT entry voltage | UINT16 | / | [100.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10392 | HVRT exit voltage | UINT16 | / | [100.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10393 | LVRT entry voltage | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10394 | LVRT exit voltage | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10395 |  | UINT16 | / | [0.0,110.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10396 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10397 |  | UINT16 | / | [20.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10398 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10399 |  | UINT16 | / | [0.0,15.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10400 |  | / | / | / | 10 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10410 | P-F mode | ENUM | / | 0-关闭；1-线性；2-滞回 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10411 |  | UINT16 | / | / | 1 | 0.01 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10412 |  | UINT16 | / | / | 1 | 0.01 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10413 |  | UINT16 | / | / | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10414 |  | UINT16 | / | / | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10415 |  | UINT16 | / | / | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10416 |  | UINT16 | / | / | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10417 |  | UINT16 | / | / | 1 | 1 | %/s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10418 |  | UINT16 | / | / | 1 | 1 | %/s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10419 | P-F mode HF1 | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10420 | P-F mode HP1 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10421 | P-F mode HF2 | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10422 | P-F mode HP2 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10423 | P-F mode HF3 | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10424 | P-F mode HP3 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10425 | P-F mode LF1 | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10426 | P-F mode LP1 | INT16 | / | [-135.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10427 | P-F mode LF2 | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10428 | P-F mode LP2 | INT16 | / | [-135.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10429 | P-F mode LF3 | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10430 | P-F mode LP3 | INT16 | / | [-135.0,135.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x10 | 10431 | P-F mode hysteresis time | UINT32 | / | [0.00,600.00] | 2 | 0.01 | s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x10 | 10433 |  | UINT32 | / | / | 2 | 0.01 | %/s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10435 | H-PF active power reduction slope | UINT16 | / | [2,12] | 1 | 1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10436 | L-PF active power rise slope | UINT16 | / | [2,12] | 1 | 1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10437 |  | / | / | / | 12 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10449 | P-Q mode | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10450 | P-Q mode P1 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10451 | P-Q mode Q1 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10452 | P-Q mode P2 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10453 | P-Q mode Q2 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10454 | P-Q mode P3 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10455 | P-Q mode Q3 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10456 | P-Q mode P4 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10457 | P-Q mode Q4 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10458 | P-Q mode P5 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10459 | P-Q mode Q5 | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10460 | P-Q mode P1' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10461 | P-Q mode Q1' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10462 | P-Q mode P2' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10463 | P-Q mode Q2' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10464 | P-Q mode P3' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10465 | P-Q mode Q3' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10466 | P-Q mode P4' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10467 | P-Q mode Q4' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10468 | P-Q mode P5' | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10469 | P-Q mode Q5' | INT16 | / | [-100.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10470 | P-Q mode power priority | ENUM | / | 0-有功优先；1-无功优先 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10471 | P-Q mode power reference | ENUM | / | 0-最大有功功率百分比； 1-最大无功功率百分比； 2-可用无功功率百分比； 3-视在功率百分比 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x10 | 10472 | P-Q mode response time | UINT32 | / | [0.00,200.00] | 2 | 0.01 | s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10474 |  | UINT16 | / | [0.0,130.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10475 |  | UINT16 | / | [0.0,130.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10476 |  | UINT16 | / | [0,10] | 1 | 1 | / | / | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10477 | P-Q mode voltage lock function | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10478 |  | / | / | / | 6 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10484 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10485 |  | UINT16 | / | [0.3,20.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10486 |  | INT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10487 |  | INT16 | / | [-100.0,0.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10488 |  | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10489 |  | UINT16 | / | [45.00,65.00] | 1 | 0.01 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10490 |  | / | / | / | 4 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10494 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10495 |  | UINT16 | / | [0.03,0.10] | 1 | 0.01 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10496 |  | UINT16 | / | [4.0,14.0] | 1 | 0.1 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10497 | SPF mode | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10498 | SPF mode power reference | ENUM | / | 0-额定功率；1-最大有功功率 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x10 | 10499 | SPF mode response time | UINT32 | / | [0.00,200.00] | 2 | 0.01 | s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10501 | SPF mode voltage lock function | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10502 | SPF mode voltage lock entry point | UINT16 | / | [0.0,130.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10503 | SPF mode voltage lock exit point | UINT16 | / | [0.0,130.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10504 | SPF mode P1 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10505 | SPF mode PF1 | INT16 | / | [-1.000,0.000)(0.000,1.000] | 1 | 0.001 | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10506 | SPF mode P2 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10507 | SPF mode PF2 | INT16 | / | [-1.000,0.000)(0.000,1.000] | 1 | 0.001 | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10508 | SPF mode P3 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10509 | SPF mode PF3 | INT16 | / | [-1.000,0.000)(0.000,1.000] | 1 | 0.001 | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10510 | SPF mode P4 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10511 | SPF mode PF4 | INT16 | / | [-1.000,0.000)(0.000,1.000] | 1 | 0.001 | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10512 | SPF mode P5 | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10513 | SPF mode PF5 | INT16 | / | [-1.000,0.000)(0.000,1.000] | 1 | 0.001 | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10514 |  | / | / | / | 8 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10522 | LFSM mode | ENUM | / | 0-关闭；1-线性；2-滞回 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10523 | LFSM-O slope s | UINT16 | / | [2.0,12.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10524 | LFSM-U slope s | UINT16 | / | [2.0,12.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10525 | LFSM-O entry point | UINT16 | / | [60.000,65.000],[50.000,55.000] | 1 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10526 | LFSM-O exit point | UINT16 | / | [60.000,65.000],[50.000,55.000] | 1 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10527 | LFSM-U entry point | UINT16 | / | [55.000,60.000],[45.000,50.000] | 1 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10528 | LFSM-U exit point | UINT16 | / | [55.000,60.000],[45.000,50.000] | 1 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10529 | LFSM mode exit rate | UINT16 | / | [0.00,125.00] | 1 | 0.01 | %/s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10530 | LFSM mode hysteresis time | UINT16 | / | [0.00,600.00] | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10531 | LFSM mode delay time | UINT16 | / | [0.00,2.00] | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10532 | LFSM-O end point | UINT16 | / | [60.000,65.000],[50.000,55.000] | 1 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10533 | LFSM-U end point | UINT16 | / | [55.000,60.000],[45.000,50.000] | 1 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10534 | LFSM active power max. variation | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10535 | LFSM-O active power max. variation | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10536 | LFSM-U active power max. variation | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10537 | FSM mode | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10538 | FSM mode active power max. change | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10539 | FSM mode dead zone | UINT16 | / | [0.000,1.000] | 1 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10540 | FSM mode slope | UINT16 | / | [2.0,12.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10541 | FSM mode insensitivity | UINT16 | / | [0.010,0.050] | 1 | 0.001 | Hz | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10542 |  | / | / | / | 2 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10543 | FSM-O active power max. variation | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10544 | FSM-U active power max. variation | UINT16 | / | [0.0,100.0] | 1 | 0.1 | % | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10545 |  | / | / | / | 2 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10547 | ROCOF protection function | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10548 | ROCOF level Ⅰ protection value | UINT16 | / | [0.1,4.0] | 1 | 0.1 | Hz/s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10549 | ROCOF level Ⅰ protection time | UINT16 | / | [0.01,10.00] | 1 | 0.01 | s | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 10550 | ROCOF level Ⅱ protection value | UINT16 | / | [0.1,4.0] | 1 | 0.1 | Hz/s | RW | 在线生效 | / | ○ | / | / | / |  | 运维 |  | /
| 0x06 | 10551 | ROCOF level Ⅱ protection time | UINT16 | / | [0.01,10.00] | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / |  | 运维 |  | /
| 0x06 | 10552 | ROCOF level Ⅲ protection value | UINT16 | / | [0.1,4.0] | 1 | 0.1 | Hz/s | RW | 在线生效 | / | ○ | / | / | / |  | 运维 |  | /
| 0x06 | 10553 | ROCOF level Ⅲ protection time | UINT16 | / | [0.01,10.00] | 1 | 0.01 | s | RW | 在线生效 | / | ○ | / | / | / |  | 运维 |  | /
| 0x06 | 10554 |  | / | / | / | 6 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10560 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10561 |  | UINT16 | / | / | 1 | / | / | RO | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10562 |  | / | / | / | 130 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 10692 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10693 |  | UINT16 | / | / | 1 | 0.01 | / | RW | 在线生效 | / | ○ | / | / | / | / | 运维 | / | /
| 0x06 | 10694 |  | / | / | / | 1306 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
特殊设置功能 | 0x10 | 19000 |  | MLB | / | 寄存器19000-19001必须一次性写入，否则设置无效。 | 2 | 1 | kW | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| / | / |  | INT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | INT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x10 | 19002 |  | MLB | / | 寄存器19002-19003必须一次性写入，否则设置无效。 | 2 | 1 | kvar | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| / | / |  | INT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | INT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x10 | 19004 |  | MLB | / | 寄存器19004-19007必须一次性写入，否则设置无效。 | 4 | 0.1 | A | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| / | / |  | UINT16 | / | / | / | / | / | RW | / | / | ○ | / | / | / | / | / | / | /
| 0x10 | 19008 |  | / | / | / | 192 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 19200 | Unit 1 active power | INT16 | / | / | 1 | 0.1 | kW | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 19201 | Unit 1 reactive power | INT16 | / | / | 1 | 0.1 | kvar | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 19202 | Unit 2 active power | INT16 | / | / | 1 | 0.1 | kW | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 19203 | Unit 2 reactive power | INT16 | / | / | 1 | 0.1 | kvar | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 19204 |  | / | / | / | 796 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
Internal information | 0x06 | 20000 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20001 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20002 | Restore manufacturer setting | ENUM | / | 0-无效；1-动作 | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 20003 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20004 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20005 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20006 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 关机生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20007 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20008 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20009 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 关机生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20010 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20011 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20012 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20013 |  | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 在线生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20014 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 20015 |  | ENUM | / | 0-禁止；1-使能 | 1 | / | / | RW | 关机生效 | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20016 | Insulation impedance protection value | UINT16 | / | / | 1 | 1 | kΩ | RW | 在线生效 | / | √ | 10 | 10000 | 90 | / | 运维 | / | /
| 0x06 | 20017 | Access control detection | ENUM | / | 0-Disable;1-Alarm;2-Protect | 1 | / | / | RW | Effective after shutdown | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20018 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20019 |  | UINT16 | / | / | 1 | 0.1 | / | RW | 在线生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20020 |  | UINT16 | / | / | 1 | 0.1 | / | RW | 在线生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20021 |  | UINT16 | / | / | 1 | 0.0001 | / | RW | 在线生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20022 |  | UINT16 | / | / | 1 | 0.0001 | / | RW | 在线生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20023 |  | UINT16 | / | / | 1 | 0.0001 | / | RW | 在线生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20024 |  | INT16 | / | / | 1 | 0.0001 | / | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20025 |  | INT16 | / | / | 1 | 0.0001 | / | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20026 |  | INT16 | / | / | 1 | 0.0001 | / | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20027 |  | UINT16 | / | / | 1 | 0.0001 | / | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20028 |  | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 20029 |  | UINT16 | / | / | 1 | 0.1 | % | RW | 关机生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 20030 |  | UINT16 | / | / | 1 | 0.1 | s | RW | 关机生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 20031 |  | UINT16 | / | / | 1 | 0.1 | s | RW | 关机生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 20032 |  | ENUM | / | 0-禁止；1-告警；2-保护 | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20033 |  | ENUM | / | 0-禁止；1-告警；2-保护 | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x06 | 20034 |  | / | / | / | 120 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20154 | Grid rated voltage | UINT16 | / | / | 1 | 1 | V | RW | 关机生效 | / | √ | 270 | 1000 | 690 | / | 运维 | / | /
| 0x06 | 20155 |  | / | / | / | 20 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20156 | Leakage current protection function | ENUM | / | 0-全部开启； 1-30mA档不保护； 2-60mA档不保护； 3-150mA档不保护； 4-连续故障保护升档； | 1 | / | / | RW | 关机生效 | / | ○ | / | / | 0 | / | 运维 | / | /
| 0x06 | 20157 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20158 |  | / | / | / | 1 | / | / | / | / | / | ○ | / | / | / | / | / | / | /
| 0x06 | 20159 |  | ENUM | / | 0-000(科华)；1-001(F客户)；2-002(W客户) | 1 | / | / | RW | 关机生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 20160 |  | ENUM | / | bit14~bit15：不同客户；bit8~bit13：大版本；bit0~bit7：小版本 | 1 | / | / | RW | 关机生效 | / | ○ | / | / | / | / | 厂家 | / | /
| 0x06 | 20161 |  | ENUM | / | 0-000(科华)；1-001(F客户)；2-002(W客户) | 1 | / | / | RW | 重启生效 | / | √ | / | / | / | / | 厂家 | / | /
| 0x10 | 20162 | Total charged energy calibration | UINT32 | / | / | 2 | 1 | kWh | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x10 | 20164 | Total discharged energy calibration | UINT32 | / | / | 2 | 1 | kWh | RW | 在线生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 20166 | G99 display mode | ENUM | / | 0-关闭；1-开启 | 1 | / | / | RW | 关机生效 | / | √ | / | / | / | / | 运维 | / | /
| 0x06 | 20167 |  | / | / | / | 19833 | / | / | / | / | / | ○ | / | / | / | / | / | / | /

## 3-Alarm information
Module description
|  |  | ID | Function name |  |  | Function description
|  | Return to contents | 3 | Alarm information function
Point table definition
Point type | Function code | Address | Name | Data type | Bit sequence | Status definition | Number of registers | Precision | Unit | Read/Write attribute | Effective mode | Remarks (noun explanation, special treatment, etc.) | BCS1250K-C-HUD(V1.0)
[13 empty] | Enable | Min. value | Max. value | Default value | Option range | Permission level | Alarm level | Remarks
Alarm 1 | / | / | Alarm 1 | Bitfield16 | / | / | / | / | / | RO | / | / | / | / | / | / | / | / | / | /
|  | / | Insulation impedance abnormal | / | bit0 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | AC leakage current abnormal | / | bit1 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | DC overvoltage abnormal | / | bit2 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Grid overvoltage abnormal | / | bit3 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Grid undervoltage abnormal | / | bit4 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Grid overfrequency abnormal | / | bit5 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Grid underfrequency abnormal | / | bit6 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Module overtemperature | / | bit7 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Grid phase sequence abnormal | / | bit8 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Inverter software overcurrent | / | bit9 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | DC soft start abnormal | / | bit10 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | DC switch abnormal | / | bit11 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | AC fan abnormal | / | bit12 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | AC switch abnormal | / | bit13 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Temperature switch abnormal | / | bit14 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Internal abnormal | / | bit15 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
Alarm 2 | / | / | Alarm 2 | Bitfield16 | / | / | / | / | / | RO | / | / | / | / | / | / | / | / | / | /
|  | / | Internal overtemperature | / | bit0 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | AC soft start abnormal | / | bit1 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Heat exchanger abnormal | / | bit2 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | AC SPD abnormal | / | bit3 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Internal emergency stop | / | bit4 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | External emergency stop | / | bit5 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Bus voltage does not meet power-on condition | / | bit6 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Bus overcurrent | / | bit7 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Zero-offset calibration abnormal | / | bit8 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Access control alarm | / | bit9 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Phase lock abnormal | / | bit10 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | DC SPD abnormal | / | bit11 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Smart meter communication abnormal | / | bit12 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Inverter hardware overcurrent | / | bit13 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Drive abnormal | / | bit14 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | ID conflict | / | bit15 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
Alarm 3 | / | / | Alarm 3 | Bitfield16 | / | / | / | / | / | RO | / | / | / | / | / | / | / | / | / | /
|  | / | Information sharing CAN communication abnormal | / | bit0 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | System sync abnormal | / | bit1 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Synchronous CAN communication abnormal | / | bit2 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | DC arc abnormal | / | bit3 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Zero sequence overcurrent | / | bit4 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | DC main contactor abnormal | / | bit5 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Smoke alarm | / | bit6 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Parallel communication abnormal | / | bit7 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | HMI CAN communication abnormal | / | bit8 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Model setting error | / | bit9 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | HMI RS485 communication abnormal | / | bit10 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Remote communication abnormal | / | bit11 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Total fault | / | bit12 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Total alarm | / | bit13 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | DC parallel mode setting error | / | bit14 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | System parameters mismatch | / | bit15 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
Alarm 4 | / | / | Alarm 4 | Bitfield16 | / | / | / | / | / | RO | / | / | / | / | / | / | / | / | / | /
|  | / | Grid voltage unbalance alarm | / | bit0 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | LVRT operation | / | bit1 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | HVRT operation | / | bit2 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | DC fan abnormal | / | bit3 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Heat sink temperature switch abnormal | / | bit4 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | External temperature switch abnormal | / | bit5 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Auxiliary power transformer temperature switch abnormal | / | bit6 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Inductor temperature switch fault | / | bit7 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Positive grounding abnormal | / | bit8 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Negative grounding abnormal | / | bit9 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | AC grounding abnormal | / | bit10 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Grid-tied grounding abnormal | / | bit11 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | BMS emergency stop | / | bit12 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Air-to-air heat exchanger abnormal | / | bit13 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Grid over/under frequency standby alarm | / | bit14 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Power module overtemperature alarm | / | bit15 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
Alarm 5 | / | / | Alarm 5 | Bitfield16 | / | / | / | / | / | RO | / | / | / | / | / | / | / | / | / | /
|  | / | Battery overvoltage | / | bit0 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Battery light load undervoltage | / | bit1 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | DC overcurrent | / | bit2 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Output voltage abnormal | / | bit3 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Output voltage does not meet off-grid conditions | / | bit4 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Overload protection | / | bit5 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Short circuit protection | / | bit6 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Internal fan abnormal | / | bit7 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | DC fuse abnormal | / | bit8 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Battery heavy load undervoltage | / | bit9 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Battery low voltage alarm | / | bit10 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | External fan abnormal | / | bit11 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Battery reverse connection | / | bit12 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Battery voltage does not meet charge conditions | / | bit13 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Overload alarm | / | bit14 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | DC arc module communication abnormal | / | bit15 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
Alarm 6 | / | / | Alarm 6 | Bitfield16 | / | / | / | / | / | RO | / | / | / | / | / | / | / | / | / | /
|  | / | BMS system fault | / | bit0 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | BMS communication abnormal | / | bit1 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | BMS dry contact abnormal | / | bit2 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | BMS charge disabled | / | bit3 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | BMS discharge disabled | / | bit4 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | BMS standby | / | bit5 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | BMU alarm | / | bit6 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Inductor fan abnormal | / | bit7 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Heat sink overtemperature alarm | / | bit8 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Total faults | / | bit9 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Total alarms | / | bit10 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | AC fan lifespan abnormal | / | bit11 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | DC fan lifespan abnormal | / | bit12 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | AC switch lifespan abnormal | / | bit13 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | DC switch lifespan abnormal | / | bit14 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Liquid-cooling unit abnormal | / | bit15 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
Alarm 7 | / | / | Alarm 7 | Bitfield16 | / | / | / | / | / | RO | / | / | / | / | / | / | / | / | / | /
|  | / | Grid-volt does not meet the startup | / | bit0 | / | / | / | / | / | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Grid-fre does not meet the startup | / | bit1 | / | / | / | / | / | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | AC/DC copper bar overtemperature alarm | / | bit2 | / | / | / | / | / | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | Anti-islanding abnormal | / | bit3 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | System linkage fault | / | bit4 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit5 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Grounding circuit abnormal | / | bit6 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Neutral point contactor abnormal | / | bit7 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | AC buffer abnormal | / | bit8 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | AC/DC copper bar overtemperature protection | / | bit9 | / | / | / | / | / | / | / | √ | / | / | / | / | Customer | Important | /
|  | / | System over-temperature | / | bit10 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | System over-humidity | / | bit11 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | PV polarity reverse connected | / | bit12 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Compact substation over-temperature | / | bit13 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Bus neutral wire overcurrent | / | bit14 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Internal overhumidity | / | bit15 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Liquid cooler 1 abnormal | / | bit0 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Liquid cooler 2 abnormal | / | bit1 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Pump 1 abnormal | / | bit2 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Pump 2 abnormal | / | bit3 | 0-Normal; 1-Abnormal | / | / | / | RO | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Cooling liquid temperature abnormal | / | bit4 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Water inlet and outlet pressure abnormal | / | bit5 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit6 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit7 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit8 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit9 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit10 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit11 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit12 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit13 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit14 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /
|  | / | Reserved | / | bit15 | / | / | / | / | / | / | / | ○ | / | / | / | / | Customer | Important | /