## Inputs
ANARITA 10 MW BESS — FINANCIAL MODEL (4-HOUR, 2×5/20)
Prepared for: Muminjon (Spanercom) ¦ Lighthief Cyprus Ltd ¦ 24 March 2026 — matches commercial offer €119k/MWh turnkey (€4.76M, 40 MWh total)
⚡ Yellow cells are modifiable inputs — change them to run your own scenarios
INPUT PARAMETERS
Parameter | Value | Unit | Source / Notes
PV Installed Capacity | 10 | MW | Client
Annual Specific Yield | 1932 | kWh/kWp | PVSyst verified (May-24 to Oct-25)
Annual PV Production |  | MWh | Calculated: capacity × yield
Park Configuration | Fixed Tilt (EAST + WEST) |  | Client confirmed
PV Annual Degradation | 0.5% |  | Industry standard (0.5%/yr)
Peak Discharge Price | 182.99 | €/MWh | TSOC DAM 134-day avg (17:00-21:00)
Round-Trip Efficiency | 86.32% |  | Linyang AC-AC full system
Net Revenue per MWh Stored |  | €/MWh | Calculated: peak price × RTE
BESS Availability | 97% |  | Guaranteed LTSA Tier C (97%)
LTSA Cost Rate | 2469.59 | €/MWh/yr | Confirmed Linyang RFI V3
Insurance (annual) | 15000 | €/yr | Budget estimate
Cycles per Day | 1 |  | Annual average (conservative)
BESS EOL Definition | 70% |  | SOH threshold (70%)
BESS OPTIONS
Option | Power (MW) | Energy (MWh) | Price (€) | EUR/kWh | Configuration
Option A | 10 | 20 | 3033000 |  | 4 x 5 MWh (2 per park)
Option B | 10 | 30 | 4440000 | 148 | 6 x 5 MWh (3 per park)
Selected offer (this workbook) | 10 | 40 | 4760000 |  | 8 x 5 MWh (4 per park)

## Scenario Matrix
YEAR 1 SCENARIO ANALYSIS
Primary curtailment cases: B=50%, C=60%, D=70%. E and F repeat 50% and 70% so legacy option-block formulas stay valid.
Curtailment Rate | 50% | 60% | 70% | 50% | 70%
Annual Curtailed (MWh)
Avg Daily Curtailed (MWh)
OPTION A: 10 MW / 20 MWh
BESS Price (€)
Annual O&M + Insurance (€)
Max Annual Throughput (MWh)
Ratio (daily curt / BESS MWh)
Capture Efficiency
Annual Captured (MWh)
Annual Discharged (MWh)
Gross Revenue (€)
Net Income (€)
ROI (%)
Simple Payback (years)
OPTION B: 2 × 5 MW / 15 MWh (30 MWh total)
BESS Price (€)
Annual O&M + Insurance (€)
Max Annual Throughput (MWh)
Ratio (daily curt / BESS MWh)
Capture Efficiency
Annual Captured (MWh)
Annual Discharged (MWh)
Gross Revenue (€)
Net Income (€)
ROI (%)
Simple Payback (years)
OPTION: 2 × 5 MW / 20 MWh (40 MWh total, 4-hour)
BESS Price (€)
Annual O&M + Insurance (€)
Max Annual Throughput (MWh)
Ratio (daily curt / BESS MWh)
Capture Efficiency
Annual Captured (MWh)
Annual Discharged (MWh)
Gross Revenue (€)
Net Income (€)
ROI (%)
Simple Payback (years)

## 15-Year Projection
15-YEAR PROJECTION — OPTION B (30 MWh)
Curtailment Rate: | 50% | ← Change this to model different scenarios
BESS Option: | B (30 MWh)
Year | PV (MWh) | SOH % | Eff BESS (MWh) | Curtailed (MWh) | Ratio | CE | Captured (MWh) | Dischgd (MWh) | Revenue (€) | O&M (€) | Net (€) | Cumul. (€) | SOH Data
1 | [12 empty] | 100%
2 | [12 empty] | 94.62%
3 | [12 empty] | 92.66%
4 | [12 empty] | 90.7%
5 | [12 empty] | 88.74%
6 | [12 empty] | 86.78%
7 | [12 empty] | 85.34%
8 | [12 empty] | 83.9%
9 | [12 empty] | 82.46%
10 | [12 empty] | 81.02%
11 | [12 empty] | 79.58%
12 | [12 empty] | 78.39%
13 | [12 empty] | 77.2%
14 | [12 empty] | 76.01%
15 | [12 empty] | 74.82%
[11 empty] | 73.61% |  | 73.61%
SUMMARY
Total Revenue (€)
Total O&M (€)
Total Net Income (€)
BESS Investment (€)
Return Multiple
Annualised ROI

## LCOS
LEVELIZED COST OF STORAGE
Cost Component | Option A (20 MWh) | Option B (30 MWh) | Option C (40 MWh)
Capital (BESS EPC)
O&M — LTSA 15 years
Ext. Warranty Yr 6-10 (€1,661.68/MWh×5)
Ext. Warranty Yr 11-15 (€2,083.72/MWh×5)
TOTAL 15-YEAR COST
SYSTEM LCOS (full utilisation)
15-Year Discharged (MWh)
System LCOS (€/MWh)
REVENUE MARGIN
Revenue per MWh Discharged
System LCOS
Margin per MWh (€)
Margin %
DISCOUNTED LCOS (8% WACC)
Discount Rate | 8% | ← Modifiable
NPV of Total Costs (€)
NPV of Energy Discharged (MWh)
Discounted LCOS (€/MWh)
Discounted Margin per MWh (€)
Discounted Margin %

## Park Data
ACTUAL PARK CURTAILMENT DATA — Spanercom Anarita
Source: energy_production_Oct2025.xlsx ¦ EAST + WEST combined ¦ Fixed tilt
Month | Energy Yield (MWh) | Est. Potential (MWh) | PVSyst (MWh) | Curtailment %
May-24 | 1023 | 1854 | 1921 | 45%
Jun-24 | 1670 | 1888 | 1987 | 12%
Jul-24 | 1791 | 1916 | 2034 | 7%
Aug-24 | 1703 | 1788 | 1944 | 5%
Sep-24 | 1225 | 1589 | 1724 | 23%
Oct-24 | 941 | 1617 | 1461 | 42%
Nov-24 | 645 | 1160 | 1108 | 44%
Dec-24 | 694 | 951 | 922 | 27%
Jan-25 | 600 | 1179 | 955 | 49%
Feb-25 | 655 | 1198 | 1086 | 45%
Mar-25 | 566 | 1648 | 1513 | 66%
Apr-25 | 578 | 1731 | 1669 | 67%
May-25 | 850 | 1769 | 1921 | 52%
Jun-25 | 1376 | 1898 | 1987 | 28%
Jul-25 | 1438 | 1968 | 2034 | 27%
Aug-25 | 1147 | 1878 | 1944 | 39%
Sep-25 | 965 | 1725 | 1724 | 44%
Oct-25 | 467 | 1139 | 1461 | 59%
CURTAILMENT TREND
Period | Avg Curtailment | Notes
May-Aug 2024 | 18% | Low — early market
Sep-Dec 2024 | 34% | Increasing
Jan-Apr 2025 | 57% | High — spring peak
May-Oct 2025 | 42% | Summer lower, still elevated
Full 2025 (Jan-Oct) | 48% | Current baseline

## Formula Reference
FORMULA REFERENCE & METHODOLOGY
All formulas used in this model, with descriptions and cell references
INPUT CALCULATIONS
Calculation | Formula (text representation) | Description
Annual PV Production (MWh) | PV_MW × Specific_Yield [Inputs!B9] = B7 × B8 | 10 MW × 1,932 kWh/kWp = 19,320 MWh. Units: MW × kWh/kWp = MWh (since 1 MW = 1000 kWp).
Net Revenue per MWh Stored | Peak_Price × RTE [Inputs!B14] = B12 × B13 | €182.99 × 86.32% = €157.96/MWh. Revenue after round-trip losses on each MWh stored.
Annual O&M Cost | BESS_MWh × LTSA_Rate + Insurance [Scenario Matrix] = Inputs!C24 × Inputs!B16 + Inputs!B17 | e.g. 30 MWh × €2,469.59 + €15,000 = €89,088/yr. LTSA rate is OEM-confirmed (Linyang RFI V3).
SCENARIO MATRIX FORMULAS
Calculation | Formula (text representation) | Description
Annual Curtailed Energy | Annual_PV_Production × Curtailment_Rate [Row 5] = Inputs!B9 × [curtailment %] | Total energy the DSO orders curtailed per year. e.g. 19,320 MWh × 50% = 9,660 MWh
Avg Daily Curtailed | Annual_Curtailed / 365 [Row 6] = [Row 5] / 365 | Average daily curtailment in MWh. Used to calculate the ratio for CE lookup.
Max Annual Throughput | BESS_MWh × 365 × Availability [Row 11/25/39] = Inputs!C[option] × 365 × Inputs!B15 | Maximum energy the BESS can cycle in a year. e.g. 20 MWh × 365 × 97% = 7,081 MWh
Ratio | Avg_Daily_Curtailed / BESS_MWh [Row 12/26/40] = [Row 6] / Inputs!C[option] | How much daily curtailment vs BESS capacity. Ratio > 1 = more curtailment than battery can absorb.
Capture Efficiency (CE) | IF(Ratio>1.5, 0.97, IF(Ratio>1.2, 0.95, IF(Ratio>1.0, 0.92, IF(Ratio>0.8, 0.88, IF(Ratio>0.6, 0.82, 0.72))))) | Accounts for temporal mismatch: not all curtailment occurs when BESS is available. Higher ratio = more days the BESS fills = higher efficiency.
Annual Captured | MIN( Max_Throughput, Annual_Curtailed × CE × Availability ) [Row 14/28/42] = MIN([throughput], [curtailed] × [CE] × Inputs!B15) | The lesser of: BESS cycling limit OR available curtailed energy adjusted for capture efficiency and ~11 days/yr downtime.
Annual Discharged | Annual_Captured × RTE [Row 15/29/43] = [captured] × Inputs!B13 | Energy actually delivered to grid after round-trip losses. RTE = 86.32% AC-AC full system.
Gross Revenue | Annual_Discharged × Peak_Price [Row 16/30/44] = [discharged] × Inputs!B12 | Total revenue from selling discharged energy at evening peak prices. €182.99/MWh avg (17:00-21:00).
Net Income | Gross_Revenue − Annual_O&M [Row 17/31/45] = [revenue] − $B$[O&M row] | Revenue minus operating costs. O&M referenced with absolute $ to column B.
ROI (%) | Net_Income / BESS_Price [Row 18/32/46] = [net] / $B$[price row] | Simple annual return on investment. e.g. €1,054,101 / €3,033,000 = 34.8%
Simple Payback (years) | BESS_Price / Net_Income [Row 19/33/47] = $B$[price row] / [net income] | Years to recover the initial investment. e.g. €3,033,000 / €1,054,101 = 2.9 years
15-YEAR PROJECTION FORMULAS
Calculation | Formula (text representation) | Description
PV Production (Year N) | Base_PV × (1 − Degradation)^(N−1) [Col B] = Inputs!B9 × (1 − Inputs!B11)^(year−1) | PV output declines 0.5%/yr. Year 1 = 19,320 MWh → Year 15 ≈ 17,996 MWh.
SOH % (Year N) | Hardcoded from Linyang degradation curve [Col C] = $O$[row] (lookup to SOH data column) | State of Health at 1 cycle/day, 0.25P rate. Year 1: 94.62%, Year 5: 86.78%, Year 10: 79.58%, Year 15: 73.61%. Source: Linyang cycle-life test data.
Effective BESS (MWh) | Nominal_BESS_MWh × SOH% [Col D] = Inputs!C25 × $O$[row] | Usable capacity decreases as cells degrade. e.g. 30 MWh × 86.78% = 26.03 MWh at Year 5.
Annual Curtailed | PV_Production × Curtailment_Rate [Col E] = B[row] × $B$3 | Curtailment rate held constant (modifiable in cell B3). PV degradation reduces available curtailment each year.
Captured | MIN( Eff_BESS × 365 × Avail, Curtailed × CE × Avail ) [Col H] = MIN(D[row]×365×Inputs!B15, E[row]×G[row]×Inputs!B15) | Same formula as scenario matrix but using year-specific effective BESS capacity and PV production.
Cumulative Net | Previous_Cumulative + Current_Year_Net [Col M] = M[prev] + L[row] | Running total. Payback year is when cumulative net exceeds BESS investment.
LCOS FORMULAS
Calculation | Formula (text representation) | Description
Total 15-Year Cost | CAPEX + (O&M × 15) + Ext_Warranty_6to10 + Ext_Warranty_11to15 [LCOS sheet Row 8] = SUM(rows 4:7) | Sum of capital, operating, and warranty costs over 15 years.
15-Year Discharged (System) | BESS_MWh × 365 × Avail × RTE × SUM(SOH_yr1..yr15) [LCOS Row 11] = [MWh] × 365 × B15 × B13 × SUM('15-Year Projection'!O8:O22) | Total energy delivered assuming 1 full cycle per available day, declining with SOH.
System LCOS | Total_15yr_Cost / Total_15yr_Discharged [LCOS Row 12] = [Row 8] / [Row 11] | Cost per MWh delivered at full utilisation. Intrinsic cost of the storage technology.
Margin per MWh | Peak_Discharge_Price − LCOS [LCOS Row 17] = Inputs!B12 − [LCOS] | Profit per MWh discharged. Driven by €0 charge cost under curtailment recovery.
Discounted LCOS | NPV(All_Costs) / NPV(All_Energy_Discharged) [LCOS Row 25] = [NPV costs] / [NPV energy] | Levelized cost with time-value-of-money. Discount rate (default 8%) weights early costs more heavily. More rigorous for investor analysis.
NPV of Costs | CAPEX + SUMPRODUCT(Annual_Cost / (1+r)^{1..15}) [LCOS Row 23] = CAPEX + discounted O&M + discounted warranties | Present value of all future costs discounted at WACC. Includes O&M (yr 1-15) + ext warranty (yr 6-15).
NPV of Energy | SUM( Discharged_yr_n / (1+r)^n ) for n=1..15 [LCOS Row 24] = sum of SOH-adjusted discharged per year, each discounted | Present value of energy delivered, using SOH-adjusted capacity for each year.
KEY ASSUMPTIONS & DATA SOURCES
Parameter | Value | Source
Peak Discharge Price | €182.99/MWh | TSOC DAM 134-day verified avg (Oct 2025 – Feb 2026), 17:00-21:00. Summer not yet available.
Charge Cost | €0/MWh | Curtailment recovery: energy would otherwise be wasted. Not purchased from grid.
Round-Trip Efficiency | 86.32% | Linyang AC-AC full system incl. PCS, transformers, cabling, auxiliaries. PCS-only = 87.8%.
BESS Availability | 97% | Guaranteed under LTSA Tier C. ~11 days/year downtime.
PV Degradation | 0.5%/year | Industry standard for crystalline silicon. Linear degradation.
SOH Degradation | See SOH curve (col O) | Linyang cycle-life data at 0.25P, 1 cycle/day. EOL = 70% SOH.
Cycles per Day | 1 (annual average) | Conservative. Winter ~0.7-0.8; summer constrained by BESS capacity.
Curtailment Rate | Modifiable (45-70%) | Current park baseline: 48% (2025 avg). Trend: 0% (2021) → 48% (2025).
PV Production | 19,320 MWh/yr | PVSyst verified, 18 months meter data. Fixed tilt, EAST+WEST.
LTSA Rate | €2,469.59/MWh/yr | OEM-confirmed (Linyang RFI V3, Feb 2026). Preventive + corrective.
Ext Warranty Yr 6-10 | €1,661.68/MWh/yr | BESS: €913.92 + PCS/MV: €747.76. OEM-confirmed.
Ext Warranty Yr 11-15 | €2,083.72/MWh/yr | BESS: €1,157.62 + PCS/MV: €926.10. OEM-confirmed.
Discount Rate (LCOS) | 8% (modifiable) | Typical WACC for project-financed renewables in Cyprus/EU.
Inflation | Not applied | All values in nominal 2026 EUR.
Grid Arbitrage | Excluded | BESS cannot buy from DAM grid as of Feb 2026.
FCR / aFRR | Excluded from base | Requires TSO market framework (not yet in Cyprus).
CAPTURE EFFICIENCY LOOKUP TABLE
Ratio (Daily Curtailed / BESS MWh) | Capture Efficiency | Rationale
> 1.5 | 97% | Abundant surplus — near-guaranteed full daily cycle
> 1.2 | 95% | Strong surplus — very high fill probability
> 1.0 | 92% | Surplus exceeds capacity — reliable daily fill
> 0.8 | 88% | Near-parity — occasional partial cycles
> 0.6 | 82% | Moderate shortfall — frequent partial fills
< 0.6 | 72% | Significant shortfall — many days incomplete charge