## Sheet1
BESS Project Requirement Checklist储能项目执行输入条件
1 | Project Basic Information 项目基本信息
1.1 | Project Name* 项目名称* | Greenfield site on flat agricultural land; on-site Litgrid 330 kV switchgear; container-based outdoor installation; seismic level IEEE 693-2018 (moderate); ambient range -25°C to +60°C; C5 anti-corrosion environment
1.2 | Project Location* 项目地点* | Greenfield site on flat agricultural land; on-site Litgrid 330 kV switchgear; container-based outdoor installation; seismic level IEEE 693-2018 (moderate); ambient range -25°C to +60°C; C5 anti-corrosion environment
1.3 | Site Conditions*现场条件*
1.4 | Project Delivery Time 项目交付时间 | Project Delivery Time 项目交付时间 |  | Q2 2028 |  |  | COD Time 投运时间 |  | Q4 2028 / Q1 2029 (COD)
1.5 | Delivery method and location* 交付方式和地点* | DDP project site, Lithuania (Litgrid 330 kV substation area, 56°07'29.6"N 23°30'25.2"E) — final Incoterms TBD
1.6 | Project Background Introduction* 项目背景介绍* | Grid-scale BESS project in Lithuania (EU / ENTSO-E). Lithuania synchronized with Continental Europe in Feb. 2025 after leaving BRELL. National target: 1.5 GW / 4.4 GWh by 2028. State grant scheme (€208 M) provides up to 46% CapEx subsidy. Permitting timeline 4–7 months via single-window "Energy Cells" platform. Full revenue stack: FCR, aFRR, mFRR, day-ahead, intraday, and Lithuanian capacity market.
1.7 | Client Name* 客户名称* | ETET Engineering GmbH (Germany)
1.8 |  |  | owner业主 |  | developer开发商 |  | investor投资方 |  | integrator集成方 | other其他
1.9 | Client Introduction* 客户介绍* | DDP project site, Lithuania (Litgrid 330 kV substation area, 56°07'29.6"N 23°30'25.2"E) — final Incoterms TBD
1.1 | Investor* 投资方* | Grid-scale BESS project in Lithuania (EU / ENTSO-E). Lithuania synchronized with Continental Europe in Feb. 2025 after leaving BRELL. National target: 1.5 GW / 4.4 GWh by 2028. State grant scheme (€208 M) provides up to 46% CapEx subsidy. Permitting timeline 4–7 months via single-window "Energy Cells" platform. Full revenue stack: FCR, aFRR, mFRR, day-ahead, intraday, and Lithuanian capacity market.
1.11 | Party of Construction* 建设方* | ETET Engineering GmbH (Germany)
1.12 | Operator* 运营方* | To be defined — O&M contractor under 15-year O&M agreement (candidates include OEM (CATL / Power Electronics) and specialized O&M providers)
1.13 | Capital investment* 投资总额* | Total CapEx EUR 207.5 M (Battery System EPC €130 M · Substation €37 M · RTB Rights €25 M · Grid Connection/BKZ €12.5 M). Financing: Equity 20% (€38.4 M) / Debt 80% (€153.6 M @ 4.0% p.a., 15 yrs).
1.14 | Terms of Payment Collection/Time* 回款条件/时间* | Milestone-based (down payment at PO, progress payments at delivery/installation, final payment at COD & performance test) — to be defined in EPC contract
1.15 | Terms of Payment/Time* 付款条件/时间* | Milestone-based against contractual deliverables (PO, delivery, commissioning, PAC, FAC) — to be defined in supply/EPC contract
2 | System Design Required Information系统设计所需信息
| Item 项目 | Specification 规格 | [7 empty] | Remark 备注
2.1 | Application*应用* Please specify! |  |  | Peak Shifting, Peak Shaving, Demand Response 错峰、调峰、需求响应 | [5 empty] | Please tick on the specific application scenario 请勾选具体应用场景
Load following 负载跟随（需量调节）
Frequency Regulation (FR, EFR, PCR, etc) 频率调节（FR、EFR、PCR等）
Emergency response 应急响应
Power quality improvement/Harmonic 电能质量改善/谐波
PV Integration (PV Peak shifting, PV Ramp-rate control) PV集成（PV峰值偏移、PV斜率控制）
Wind Integration (Wind Peak shifting, Wind Ramp-rate control) 风力集成（风力峰值转移、风力斜度控制）
Voltage Regulation 电压调节
Micro Grid 微电网
Others, etc 其他等
2.2 | Charge/Discharge Rate*充电/放电倍率* | 0.5C usable (up to 1.7 full cycles per day)
2.3 | Whether it is configured according to the nameplate capacity* 是否按照铭牌容量配置* | YES | YES — configured per nameplate capacity |  |  | Nameplate Power(MW)* 所需功率（MW）* |  | 500 MW AC | Nameplate Capacity (MWh)* 所需容量（MWH）* | 1,000 MWh DC
2.4 | Required Power(MW)* 所需功率（MW）* | Charging:充电： Active Power：有功功率： |  |  | Charging: 500 MW Active Power: 500 MW | Discharging:放电： Reactive Power：无功功率： |  | Discharging: 500 MW Reactive Power: ±0.95 PF capability per Litgrid grid code | AC-AC Efficiency Requirement: AC-AC效率要求： | Please specify the efficiency is included the Auxiliary Consumption or not. 请说明效率是否包括辅 助消耗。
2.5 | Required Capacity( MWh)@ POC*所需容量（MWH） | BoL (Beginning of Life) Usable Energy: 起始可用能量： |  |  |  | 1,000 MWh @ POC
|  | EoL (End of Life) Usable Energy: 终止可用能量: |  |  |  | 700 MWh (70% SoH after 15 years / 8,000 cycles)
2.6 | Special Usable Capacity Requirement* 特殊可用容量要求* | End-of-life augmentation strategy to be discussed; guaranteed usable energy verified via annual capacity test
2.7 | Installation Requirement*安装要求* | Outdoor 室外 |  |  | Container 集装箱 |  |  | Building 建筑内
2.8 | Cycle Frequency*循环频率* | Up to 1.7 full cycles per day; typical 1.0–1.5 cycles/day
2.9 | Required Battery Life* 所需电池寿命* | 15 years / 8,000 equivalent full cycles (70% SoH at end of life)
2.1 | Required Warranty* 质保* | Performance & availability warranty over 15 years (capacity guarantee curve, availability ≥ 97%); product warranty and workmanship per supplier standard — to be negotiated
2.11 | Project Lifetime* 项目运营年限* | 15 years operating period
2.12 | Corrision Protection Requirment for equipment* 设备防腐要求* | C5 anti-corrosion coating (per ISO 12944) — coastal / moderate industrial environment
2.13 | Is there a weight limit requirement* 是否有限重要求* | Containers ~45 t each (6,058 × 2,438 × 2,896 mm); road/sea transport — standard 40 ft dimensions. No special road weight restrictions expected; to be confirmed via logistics survey.
3 | Energy storage power station access information储能电站接入信息
3.2 | BESS access voltage and frequency level* BESS接入电压和频率* | 330 kV / 50 Hz, connected to Litgrid TSO grid (Continental Europe / ENTSO-E synchronous area)
3.3 | Is electricity allowed enter the grid?是否允许并网？ | YES — full grid injection allowed (day-ahead, intraday, FCR, aFRR, mFRR, capacity market)
3.4 | Scope of delivery (required if quotation is required)* 供货范围（如需报价，则必须填写）* |  | Battery system, (Including packs, battery racks, BMS, battery cabinet, DC cables and communication cables between the supplied equipment) 电池系统（包括电池组、电池架、BMS、电池柜、直流电缆和所供设备之间的通信电缆）
Container and Auxiliary System, (Including fire fighting, video , lighting, power distribution, air duct, etc.) 集装箱及辅助系统（包括消防、视频、照明、配电、风道等）
PCS, (If PCS provided by customer, the operating voltage range of the DC-side battery system needs to be specified Min Vdc～Max Vdc) (如果PCS由客户提供，直流侧电池系统的工作电压范围需要指定为最小 VDC~最大 VDC）
MV-skid 升压变流一体机
|  |  | Grid connected switchgear 并网开关设备 | [6 empty] | Generally provided by the EPC 一般由EPC方提供
|  |  | EMS 储能能量管理系统 | [6 empty] | If need to be provided by CRRC, should specify the specific functional requirements. 应说明具体的功能要求。
4 | Communication requirement通信要求
4.1 | Communication Protocol with BMS* 与BMS的通信协议* |  | CAN |  | Modbus
4.2 | Communication Interface*通信接口* |  | Ethernet(RJ45) 以太网（RJ45） |  | CAN |  | RS485 |  | Other: 其他:
4.3 | Communication Confiuration*通信配置* |  | BMS- PCS& EMS |  | BMS-PCS |  | BMS-EMS
5 | Certification Requirements认证要求
5.1 | Battery system *电池系统* | EU Battery Regulation 2023/1542 · IEC 62933 · UN38.3 · UL1973 · IEC 62619 · NFPA 855 · Lithuanian Grid Code (Litgrid) · 4-level fire safety (smoke / H2 / aerosol / sprinkler)
5.2 | PCS & Electrical* PCS和电气* | IEC 62271-212 / 200 · IEC 60076 · VDE-AR-N 4120 (DE reference) · Lithuanian Grid Code (Litgrid) · CE marking · IEC 61000 EMC
6 | If the BESS is connected to the user side or the microgrid system, the customer needs to provide the following information (must be filled in if the plan and quotation are required) 如BESS接入用户侧或微网系统，客户需提供以下资料（如需方案和报价必须填写）
6.1 | Electric bill 电费账单 | N/A — utility-scale grid-connected project (not user side / microgrid) | [7 empty] | User side must provide 用户端必须提供
6.2 | Daily load curve日负荷曲线 | N/A — grid-connected project; revenues via wholesale markets and ancillary services (FCR, aFRR, mFRR, day-ahead, intraday, capacity market) | [7 empty] | User side / micro grid required 需要用户侧/微电网
6.3 | Description of electricity consumption用电说明 | N/A — utility-scale BESS directly connected to Litgrid 330 kV grid, no user load behind the meter | [7 empty] | User side must provide 用户端必须提供
6.4 | Electrical layout of distribution room 配电室电气布置图 | N/A — 330 kV Litgrid substation on site; single-line diagram available in Virtual Data Room upon NDA signing | [7 empty] | User side must provide 用户端必须提供
6.5 | General layout of the plant 平面布置图 | General site layout available — see "Project Side Overview" of BESS Lithuania LT-01 (provided in VDR upon NDA) | [7 empty] | Please provide 请提供
Notes 备注: Data based on BESS Lithuania LT-01 Investor Pitch (June 2026) and Business Case ETET / Phelas (Min Scenario, 10.06.2026). All figures indicative and subject to final EPC contract and due diligence. Strictly confidential — for CRRC internal use only.
Y
N