## Pricing_Model_All_Projects
No |  |  |  | Project | Group Code | Client Name | BESS MW | MWh | PV MWp | Battery Sets | MV SKID SETs | Containers | Unit/kwh cif | Price Hike | CIF (EUR) | Unit_EUR_per_kWh_calc_from_MWh | Implied_MWh_from_Unit | ImportDuty | PortCustoms | A Soulis / Crane + Inland Interfreight | Inland Trnansport if separate from Crane | LV_Cabling | MV_Cabling | MV_Terminations | Protection_Eng | RemoteTrip | UPS_Aux | LPS External lightning Protection | LPS Lightning (DEHN) | SPDs Surge Protection (DEHN) | Earthing Grid (DEHN) | Protection Testing & DSO + StrikeRA Install | VOLTUS EMS (Feb 16 Update) | Civil Works (Kamil €2000/MWh) | Drainage (incl in Civil) | Commissioning | Docs_Compliance | Insurance | PCC_Bay_Extension_EUR | Adders Total (excl EMS) | Installed Cost (EUR) | Cost per MWh | Client Revenue (EUR) | Client Price/MWh | Notes | Voltus Group (NEW) | Parks in Group | EMS Total (System+HW+Config+Install) | SCADA Local (Basic €15k / Advanced €30k) | SCADA Global Share (per park) | Total EMS/SCADA (All-in) | EMS per MWh | Status | Dino Price/MWh | Dino Total | Full EPC Cost | Margin (EUR) | Margin % | Price Type | Target Price/MWh | Target Total | Target Margin % | IND ORDER PRICING >> | IND CIF (+15%) | IND Adders (+15%) | IND EMS/SCADA | IND Total EPC | IND Client (13%) | IND €/MWh | IND vs Group Diff
[18 empty] | Weighted Average 2.66 |  | based on 23k for 8 containers | [7 empty] | Customer Paid | ✅ DEHN QUOTED. LPS 20HC €429.41/cont + 40HC €617.52/SKID. HVI Light Plus, LPS III/IV. | ✅ DEHN QUOTED. DC €199.28/cont + LV €336.47/SKID + MV €498.92/park + Aux €163.74/park + Comms €134.37/struct | ✅ DEHN QUOTED. €793.59 per structure (BESS + MV). Enhancement: N/A site-dependent. | ✅ LPS/SPD Install: €1,600/park (balanced: StrikeRA £1700 GBP + local €500). Excl transport. Protection testing: client pays (Dino confirmed). | ✅ UPDATED Feb 16, 2026 — New Voltus quote: 3 groups + 6 standalone. SCADA tiered: Basic €15k / Advanced €30k. 5% discount pending. | ✅ CONFIRMED — Kamil €2,000/MWh. Platforms, trenches, cabling labour (excl cable), water trenches. Feb 2026. | Included in Kamil civil works rate |  | Docs & Statutory Compliance (EAC / CERA fees only) Estimate 7000 | 0.0075 | [6 empty] | Locked Price Presented Already
Verified | Client Name | District | PV Capacity (MW) |  |  | Park Name | [11 empty] | partially confirmed | Received notes from interface needs checking | Has been in talks with dino no negotiation | Qoute from Interfreigh. verifu if solis include or not | [6 empty] | In talks with Dhen | In talks with Dhen | talks with dhen | talks with dhen | Dino confirmed park owners pay this |  | 0 |  | TBC Linyang Provide? We need to know exactly what is needed her, is this us or on others. | Confirmed from Dino this is on Clieent\ | ✅ VERIFIED — Agent confirmed 0.75% of CIF. Feb 2026. | Confirm if under Voltus | [6 empty] | G1_ABIO / G2_ESP / G3_TIM / SA | Parks in Group | Voltus EMS (Quote) | SCADA Local | SCADA Global Share | Total EMS/SCADA | EMS/SCADA per MWh
50 | ABIO Power | Larnaca | 0.75 | Nicosia33 | ABIO | Greendorado Agrivoltaic | 0.75 | 3 | 0.75 | 1 | 1 | 2 |  |  | 446041.55 |  |  |  | 4000 | 4720 |  | 1400 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 6000 | 0 |  |  |  |  | 37521.26 | 579298.15 | 193099.38 | 628264.64 | 209421.55 | NEW - Abio #3 - SMALLEST - NEEDS LINYANG QUOTE FOR 3MWh | G1_ABIO | 4 | 26304 | 15000 | 2400 | 43704 | 14568 | ✅ Feb 16 Update | 174357 |  | 579298.15 | 48966.49 | 7.79 | 13% | 174357 | 697428 | 0.1732 |  | 585832 | 29693 | 54254 | 1970481 | 2226644 | 148443 | 264764
8 | ABIO Power | Larnaca | 1.8 | Larnaca1 | GRD | Greendorado Larnaca 1 | 1.25 | 5 | 1.8 | 1 | 1 | 2 |  |  | 564552.77 |  |  |  | 4000 | 4720 |  | 2800 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 10000 | 0 | 0 |  |  | 0 | 42921.26 | 706953.31 | 141390.66 | 770397.01 | 154079.4 |  | G1_ABIO | 3 | 26304 | 15000 | 2400 | 43704 | 8740.8 | ✅ Feb 16 Update | 146560 |  | 706953.31 | 63443.7 | 8.24 | 13% | 157608 | 788040 | 0.14793 |  | 693272 | 31303 | 59254 | 1114718 | 1259631 | 157454 | 175151
9 | ABIO Power | Larnaca | 0.75 | Larnaca2 | GRD | Greendorado Larnaca 2 | 1 | 5 | 0.75 | 1 | 1 | 2 |  |  | 560994 |  |  |  | 4000 | 4720 |  | 1400 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 10000 | 0 | 0 |  |  | 0 | 41521.26 | 702910.85 | 140582.17 | 765750.5 | 153150.1 |  | G1_ABIO | 3 | 26304 | 15000 | 2400 | 43704 | 8740.8 | ✅ Feb 16 Update | 165431 |  | 702910.85 | 62839.66 | 8.21 | 13% | 146011 | 730055 | 0.1395 |  | 645143 | 29693 | 59254 | 669779 | 756850 | 189212 | 59422
49 | ABIO Power | Nicosia | 6.1 | Nicosia32 | ABIO | Agios Sozomenos | 6 | 25 | 6.1 | 5 | 1 | 6 |  |  | 2310908.19 |  |  |  | 7000 | 14160 |  | 8400 | 3500 | 2200 | 6000 | 3000 | 2000 |  | 2764.57 | 2801.75 | 4761.54 | 1600 | 54583 | 50000 | 0 |  |  |  |  | 108187.86 | 2832515.71 | 113300.63 | 3136512.87 | 125460.51 | NEW - Abio #2 - CIF ESTIMATE - NEEDS LINYANG QUOTE | G1_ABIO | 4 | 54583 | 30000 | 2400 | 86983 | 3479.32 | ✅ Feb 16 Update | 123103 |  | 2832515.71 | 303997.16 | 9.69 | 13% | 123103 | 3077575 | 0.15948 |  | 2848146 | 53199 | 76718 | 783829 | 885727 | 177145 | 106797
22 | ABIO Power | Nicosia | 3.2 | Nicosia8 | DIA | Dianary 1 | 2.5 | 10 | 3.2 | 2 | 1 | 3 |  |  | 974457 |  |  |  | 5000 | 7080 |  | 4900 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 20000 | 0 | 0 |  |  | 0 | 59937.91 | 1179057.16 | 117905.72 | 1206300 | 120630 |  | G1_ABIO | 3 | 33374 | 30000 | 2400 | 65774 | 6577.4 | ✅ Feb 16 Update | 136106 |  | 1179057.16 | 27242.84 | 2.26 | LOCKED | 131540 | 1315400 | 0.12862 |  | 1224346 | 37582 | 66742 | 734090 | 829522 | 165904 | 99465
28 | ABIO Power | Nicosia | 1.4 | Nicosia14 | DIA | Dianary 2 | 2.5 | 10 | 1.4 | 2 | 1 | 3 |  |  | 974457 |  |  |  | 5000 | 7080 |  | 3500 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 20000 | 0 | 0 |  |  | 0 | 58537.91 | 1179057.16 | 117905.72 | 1206300 | 120630 |  | G1_ABIO | 3 | 33374 | 30000 | 2400 | 65774 | 6577.4 | ✅ Feb 16 Update | 120630 |  | 1179057.16 | 27242.84 | 2.26 | LOCKED | 120630 | 1206300 | 0.12574 |  | 1120626 | 35972 | 66742 | 773640 | 874213 | 174843 | 103820
29 | ABIO Power | Nicosia | 4.99 | Nicosia15 | DIA | Dianary 3 | 8 | 35 | 4.99 | 7 | 2 | 9 |  |  | 3303521 |  |  |  | 11000 | 21240 |  | 11200 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 4240.91 | 3939.89 | 7142.31 | 1600 | 68722 | 70000 | 0 | 0 |  |  | 0 | 152763.11 | 3774777.01 | 107850.77 | 4198621.38 | 119960.61 |  | G1_ABIO | 3 | 68722 | 30000 | 2400 | 101122 | 2889.2 | ✅ Feb 16 Update | 110895 |  | 3774777.01 | 423844.37 | 10.09 | 13% | 112146 | 3925110 | 0.1196 |  | 3799049 | 75716 | 104182 | 1272966 | 1438452 | 143845 | 176313
34 | ABIO Power | Nicosia | 0 | Nicosia20 | ELE | ELESTORE 1 | 12 | 40 | Standalone | 8 | 2 | 10 |  |  | 3781992 |  |  |  | 12000 | 23600 |  | 16800 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 4670.32 | 4273.54 | 7935.9 | 1600 | 75792 | 80000 | 0 | 0 |  |  | 0 | 173279.76 | 4306469.12 | 107661.73 | 4599600 | 114990 |  | G1_ABIO | 5 | 75792 | 30000 | 2400 | 108192 | 2704.8 | ✅ Feb 16 Update | 114990 |  | 4306469.12 | 293130.88 | 6.37 | LOCKED | 114990 | 4599600 | 0.13618 |  | 4349291 | 86020 | 116424 | 3098911 | 3501769 | 140071 | 437708
35 | ABIO Power | Nicosia | 0 | Nicosia21 | ELE | ELESTORE 2 | 12 | 40 | Standalone | 8 | 2 | 10 |  |  | 3781992 |  |  |  | 12000 | 23600 |  | 16800 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 4670.32 | 4273.54 | 7935.9 | 1600 | 75792 | 80000 | 0 | 0 |  |  | 0 | 173279.76 | 4306469.12 | 107661.73 | 4599600 | 114990 |  | G1_ABIO | 5 | 75792 | 30000 | 2400 | 108192 | 2704.8 | ✅ Feb 16 Update | 114990 |  | 4306469.12 | 293130.88 | 6.37 | LOCKED | 114990 | 4599600 | 0.13618 |  | 4349291 | 86020 | 116424 | 2978063 | 3365211 | 134608 | 287636
36 | ABIO Power | Nicosia | 0 | Nicosia22 | ELE | ELESTORE 3 | 12 | 40 | Standalone | 8 | 2 | 10 |  |  | 3781992 |  |  |  | 12000 | 23600 |  | 16800 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 4670.32 | 4273.54 | 7935.9 | 1600 | 75792 | 80000 | 0 | 0 |  |  | 0 | 173279.76 | 4306469.12 | 107661.73 | 4599600 | 114990 |  | G1_ABIO | 5 | 75792 | 30000 | 2400 | 108192 | 2704.8 | ✅ Feb 16 Update | 114990 |  | 4306469.12 | 293130.88 | 6.37 | LOCKED | 114990 | 4599600 | 0.13618 |  | 4349291 | 86020 | 116424 | 1328670 | 1501397 | 150140 | 185997
37 | ABIO Power | Nicosia | 0 | Nicosia23 | ELE | ELESTORE 4 | 12 | 40 | Standalone | 8 | 2 | 10 |  |  | 3781992 |  |  |  | 12000 | 23600 |  | 16800 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 4670.32 | 4273.54 | 7935.9 | 1600 | 75792 | 80000 | 0 | 0 |  |  | 0 | 173279.76 | 4306469.12 | 107661.73 | 4599600 | 114990 |  | G1_ABIO | 5 | 75792 | 30000 | 2400 | 108192 | 2704.8 | ✅ Feb 16 Update | 114990 |  | 4306469.12 | 293130.88 | 6.37 | LOCKED | 114990 | 4599600 | 0.13618 |  | 4349291 | 86020 | 116424 | 1223340 | 1382374 | 138237 | 176074
38 | ABIO Power | Nicosia | 0 | Nicosia24 | ELE | ELESTORE 5 | 12 | 40 | Standalone | 8 | 2 | 10 |  |  | 3781992 |  |  |  | 12000 | 23600 |  | 16800 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 4670.32 | 4273.54 | 7935.9 | 1600 | 75792 | 80000 | 0 | 0 |  |  | 0 | 173279.76 | 4306469.12 | 107661.73 | 4599600 | 114990 |  | G1_ABIO | 5 | 75792 | 30000 | 2400 | 108192 | 2704.8 | ✅ Feb 16 Update | 114990 |  | 4306469.12 | 293130.88 | 6.37 | LOCKED | 114990 | 4599600 | 0.13618 |  | 4349291 | 86020 | 116424 | 3978947 | 4496210 | 128463 | 571106
20 | ABIO Power | Nicosia | 5.58 | Nicosia6 | EAS | Easy Power 1 | 5 | 10 | 5.58 | 2 | 1 | 3 |  |  | 1104571 |  |  |  | 5000 | 7080 |  | 7000 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 20000 | 0 | 0 |  |  | 0 | 62037.91 | 1317550.43 | 131755.04 | 1361050 | 136105 |  | G1_ABIO | 4 | 33374 | 30000 | 2400 | 65774 | 6577.4 | ✅ Feb 16 Update | 136106 |  | 1317550.43 | 43499.57 | 3.2 | LOCKED | 136106 | 1361060 | 0.12698 |  | 1270257 | 39997 | 61742 | 1371996 | 1550355 | 155036 | 189295
21 | ABIO Power | Nicosia | 4.69 | Nicosia7 | EAS | Easy Power 2 | 4.5 | 10 | 4.69 | 2 | 1 | 3 |  |  | 1071159.65 |  |  |  | 5000 | 7080 |  | 4200 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 20000 | 0 | 0 |  |  | 0 | 59237.91 | 1282186.52 | 128218.65 | 1401540.18 | 140154.02 |  | G1_ABIO | 4 | 33374 | 30000 | 2400 | 65774 | 6577.4 | ✅ Feb 16 Update | 120630 |  | 1282186.52 | 119353.66 | 8.52 | 13% | 122823 | 1228230 | 0.12552 |  | 1142183 | 36777 | 61742 | 1240702 | 1401993 | 140199 | 173768
25 | ABIO Power | Nicosia | 7.94 | Nicosia11 | EAS | Easy Power 3 | 5 | 10 | 7.94 | 3 | 2 | 5 |  |  | 1104571 |  |  |  | 7000 | 11800 |  | 7000 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 2523.27 | 2605.29 | 3967.95 | 1600 | 40444 | 20000 | 0 | 0 |  |  | 0 | 78896.51 | 1359454.58 | 135945.46 | 1361050 | 136105 |  | G1_ABIO | 4 | 40444 | 30000 | 2400 | 72844 | 7284.4 | ✅ Feb 16 Update | 130792 |  | 1359454.58 | 1595.42 | 0.12 | LOCKED | 130792 | 1961880 | 0.13518 |  | 1830913 | 55430 | 69230 | 1955573 | 2209797 | 147320 | 247917
26 | ABIO Power | Nicosia | 1.83 | Nicosia12 | EAS | Easy Power 4 | 1.8 | 8 | 1.83 | 2 | 1 | 3 |  |  | 852929.32 |  |  |  | 5000 | 7080 |  | 3500 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 16000 | 0 | 0 |  |  | 0 | 54537.91 | 1032991.86 | 129123.98 | 1136948.62 | 142118.58 |  | G1_ABIO | 4 | 33374 | 15000 | 2400 | 50774 | 6346.75 | ✅ Feb 16 Update | 120630 |  | 1032991.86 | 103956.76 | 9.14 | 13% | 120630 | 1206300 | 0.12574 |  | 1120626 | 35972 | 61742 | 1218340 | 1376724 | 137672 | 170424
24 | ABIO Power | Nicosia | 2.1 | Nicosia10 | GRD | Greendorado 1 | 1.8 | 8 | 2.1 | 2 | 1 | 3 |  |  | 852929.32 |  |  |  | 5000 | 7080 |  | 4200 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 16000 | 0 | 0 |  |  | 0 | 55237.91 | 1032991.86 | 129123.98 | 1136948.62 | 142118.58 |  | G1_ABIO | 3 | 33374 | 15000 | 2400 | 50774 | 6346.75 | ✅ Feb 16 Update | 120630 |  | 1032991.86 | 103956.76 | 9.14 | 13% | 123388 | 1233880 | 0.12952 |  | 1142183 | 36777 | 66742 | 1245702 | 1407643 | 140764 | 173768
30 | ABIO Power | Nicosia | 1.8 | Nicosia16 | POL | Polemi | 1.25 | 10 | 1.8 | 3 | 1 | 4 |  |  | 829621.85 |  |  |  | 7000 | 11800 |  | 5600 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 1905.75 | 2134.45 | 3174.36 | 1600 | 40444 | 20000 | 0 | 0 |  |  | 0 | 75614.56 | 1046719.29 | 104671.93 | 1129579.41 | 112957.94 |  | G1_ABIO | 3 | 40444 | 30000 | 2400 | 72844 | 7284.4 | ✅ Feb 16 Update | 128128 |  | 1046719.29 | 82860.11 | 7.34 | 13% | 126828 | 1902420 | 0.12443 |  | 1796913 | 53820 | 74230 | 1924963 | 2175208 | 145014 | 272782
31 | ABIO Power | Nicosia | 1.57 | Nicosia17 | POT | Potamia p151 | 1.25 | 10 | 1.57 | 3 | 1 | 4 |  |  | 829621.85 |  |  |  | 7000 | 11800 |  | 5600 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 1905.75 | 2134.45 | 3174.36 | 1600 | 40444 | 20000 | 0 | 0 |  |  | 0 | 75614.56 | 1046719.29 | 104671.93 | 1129579.41 | 112957.94 |  | G1_ABIO | 3 | 40444 | 30000 | 2400 | 72844 | 7284.4 | ✅ Feb 16 Update | 128128 |  | 1046719.29 | 82860.11 | 7.34 | 13% | 126828 | 1902420 | 0.12443 |  | 1796913 | 53820 | 74230 | 1924963 | 2175208 | 145014 | 272782
32 | ABIO Power | Nicosia | 4.63 | Nicosia18 | POT | Potamia p208 | 4.5 | 20 | 4.63 | 6 | 2 | 8 |  |  | 1815300.83 |  |  |  | 9000 | 16520 |  | 9800 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 3811.5 | 3606.24 | 6348.72 | 1600 | 61652 | 40000 | 0 | 0 |  |  | 0 | 106386.46 | 2175170.31 | 108758.52 | 2395784.54 | 119789.23 |  | G1_ABIO | 3 | 61652 | 30000 | 2400 | 94052 | 4702.6 | ✅ Feb 16 Update | 110895 |  | 2175170.31 | 220614.23 | 9.21 | 13% | 108457 | 3253710 | 0.12054 |  | 3141417 | 58673 | 96694 | 3296784 | 3725366 | 124179 | 471665
27 | ABIO Power | Nicosia | 7.5 | Nicosia13 | REN | Renergetic | 5 | 10 | 7.5 | 2 | 1 | 3 |  |  | 1104571 |  |  |  | 5000 | 7080 |  | 7000 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 20000 | 0 | 0 |  |  | 0 | 62037.91 | 1317550.43 | 131755.04 | 1361050 | 136105 |  | G1_ABIO | 1 | 33374 | 30000 | 2400 | 65774 | 6577.4 | ✅ Feb 16 Update | 136106 |  | 1317550.43 | 43499.57 | 3.2 | LOCKED | 136106 | 1361060 | 0.12698 |  | 1270257 | 39997 | 106742 | 1416996 | 1601205 | 160120 | 240145
51 | ABIO Power | Nicosia | 2.4 | Nicosia34 | ABIO | Renergetic 2 | 2.4 | 10 | 2.4 | 2 | 1 | 3 |  |  | 943551.21 |  |  |  | 5000 | 7080 |  | 3500 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 20000 | 0 |  |  |  |  | 58537.91 | 1317550.43 | 131755.04 | 1361050 | 136105 | NEW - Abio #13 - NEEDS PRICE VERIFICATION | G1_ABIO | 4 | 33374 | 30000 | 2400 | 65774 | 6577.4 | ✅ Feb 16 Update | 120630 |  | 1317550.43 | 43499.57 | 3.2 | LOCKED | 120630 | 1206300 | 0.12574 |  | 1120626 | 35972 | 61742 | 1218340 | 1376724 | 137672 | 170424
33 | ABIO Power | Nicosia | 6.1 | Nicosia19 | SOL | Solarity | 5 | 10 | 6.1 | 2 | 1 | 3 |  |  | 1104571 |  |  |  | 5000 | 7080 |  | 7000 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 20000 | 0 | 0 |  |  | 0 | 62037.91 | 1317550.43 | 131755.04 | 1361050 | 136105 |  | G1_ABIO | 1 | 33374 | 30000 | 2400 | 65774 | 6577.4 | ✅ Feb 16 Update | 136106 |  | 1317550.43 | 43499.57 | 3.2 | LOCKED | 136106 | 1361060 | 0.12698 |  | 1270257 | 39997 | 106742 | 1416996 | 1601205 | 160120 | 240145
48 | ABIO Power | Nicosia | 3 | Nicosia31 | ABIO | Solartech 3 Extension | 2.5 | 10 | 3 | 2 | 1 | 3 |  |  | 974457 |  |  |  | 5000 | 7080 |  | 3500 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 20000 | 0 |  |  |  |  | 58537.91 | 1179057.16 | 117905.72 | 1206300 | 120630 | NEW - Abio #19 - NEEDS PRICE VERIFICATION | G1_ABIO | 4 | 33374 | 30000 | 2400 | 65774 | 6577.4 | ✅ Feb 16 Update | 120630 |  | 1179057.16 | 27242.84 | 2.26 | LOCKED | 120630 | 1206300 | 0.12574 |  | 1120626 | 35972 | 61742 | 1218340 | 1376724 | 137672 | 170424
23 | ABIO Power | Nicosia | 3 | Nicosia9 | WAN | Waneron | 3 | 11.28 | 3 | 2 | 1 | 3 |  |  | 1133091.32 |  |  |  | 7000 | 11800 |  | 4200 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 22560 | 0 | 0 |  |  | 0 | 75217.91 | 1346899.93 | 119406.02 | 1472980.89 | 130583.41 |  | G1_ABIO | 1 | 33374 | 30000 | 2400 | 65774 | 5831.03 | ✅ Feb 16 Update | 132924 |  | 1346899.93 | 126080.96 | 8.56 | 13% | 142133 | 1705596 | 0.15474 |  | 1549493 | 52210 | 106742 | 1708445 | 1930543 | 160879 | 236077
3 | Esperia Energy Group | Famagusta | 8 | Famagusta3 | ESP | Esperia Famagusta | 6.5 | 20 | 8 | 4 | 1 | 5 |  |  | 1951710.58 |  |  |  | 7000 | 11800 |  | 9100 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 2335.16 | 2468.1 | 3967.95 | 1600 | 47513 | 40000 | 0 | 0 |  |  | 0 | 93971.21 | 2263468.65 | 113173.43 | 2500334.24 | 125016.71 |  | G2_ESP | 4 | 47513 | 30000 | 5455 | 82968 | 4148.4 | ✅ Feb 16 Update | 115589 |  | 2263468.65 | 236865.59 | 9.47 | 13% | 117070 | 2341400 | 0.11861 |  | 2244467 | 50140 | 76718 | 1104717 | 1248330 | 166444 | 152988
5 | Esperia Energy Group | Famagusta | 5 | Famagusta5 | ESP | Esperia Famagusta 2 | 5 | 20 | 5 | 4 | 1 | 5 |  |  | 1848712.43 |  |  |  | 7000 | 11800 |  | 7000 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 2335.16 | 2468.1 | 3967.95 | 1600 | 47513 | 40000 | 0 | 0 |  |  | 0 | 91871.21 | 2263468.65 | 113173.43 | 2500334.24 | 125016.71 | 112950 | G2_ESP | 4 | 47513 | 30000 | 5455 | 82968 | 4148.4 | ✅ Feb 16 Update | 112945 |  | 2263468.65 | 236865.59 | 9.47 | 13% | 112945 | 2258900 | 0.13294 |  | 2126019 | 47725 | 76718 | 1104717 | 1248330 | 166444 | 152988
4 | Esperia Energy Group | Famagusta | 8.75 | Famagusta4 | ESP | Esperia Frenaros | 25 | 100 | 8.75 | 20 | 3 | 23 |  |  | 8782302 |  |  |  | 24000 | 51920 |  | 35000 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 10440.76 | 8748.18 | 18252.57 | 1600 | 167132 | 200000 | 0 | 0 |  |  | 0 | 372361.51 | 9906127.85 | 99061.28 | 11079434.93 | 110794.35 |  | G2_ESP | 4 | 167132 | 30000 | 5455 | 202587 | 2025.87 | ✅ Feb 16 Update | 106279 |  | 9906127.85 | 1173307.08 | 10.59 | 13% | 106279 | 10627900 | 0.1422 |  | 10099647 | 153318 | 209279 | 711955 | 804509 | 160902 | 96202
1 | Esperia Energy Group | Famagusta | 5 | Famagusta1 | GAL | Galascope 1 | 5 | 15 | 5 | 3 | 2 | 5 |  |  | 1592018 |  |  |  | 7000 | 11800 |  | 7000 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 2523.27 | 2605.29 | 3967.95 | 1600 | 40444 | 30000 | 0 | 0 |  |  | 0 | 88896.51 | 1879735.84 | 125315.72 | 2068111.53 | 137874.1 |  | G2_ESP | 2 | 40444 | 30000 | 5455 | 75899 | 5059.93 | ✅ Feb 16 Update | 130792 |  | 1879735.84 | 188375.69 | 9.11 | 13% | 130792 | 1961880 | 0.13522 |  | 1830821 | 55430 | 84230 | 2371325 | 2679597 | 133980 | 338205
2 | Esperia Energy Group | Famagusta | 2.5 | Famagusta2 | GAL | Galascope 2 | 2.5 | 8 | 2.5 | 2 | 1 | 3 |  |  | 871307.6 |  |  |  | 5000 | 7080 |  | 3500 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 16000 | 0 | 0 |  |  | 0 | 54537.91 | 1056994.66 | 132124.33 | 1161026.55 | 145128.32 |  | G2_ESP | 2 | 33374 | 15000 | 5455 | 53829 | 6728.62 | ✅ Feb 16 Update | 135560 |  | 1056994.66 | 104031.89 | 8.96 | 13% | 135560 | 1084480 | 0.12265 |  | 1002004 | 35972 | 76742 | 2250462 | 2543022 | 127151 | 284122
10 | Esperia Energy Group | Limassol | 8 | Limassol1 | ESP | Esperia Limassol | 8 | 60 | 8 | 12 | 2 | 14 |  |  | 4937363 |  |  |  | 16000 | 33040 |  | 11200 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 6387.96 | 5608.14 | 11110.26 | 1600 | 107323 | 120000 | 0 | 0 |  |  | 0 | 227346.36 | 5616186.33 | 93603.11 | 6003120 | 100052 |  | G2_ESP | 4 | 107323 | 30000 | 5455 | 142778 | 2379.63 | ✅ Feb 16 Update | 100052 |  | 5616186.33 | 386933.67 | 6.45 | LOCKED | 100052 | 6003120 | 0.14027 |  | 5677967 | 95036 | 149375 | 10462244 | 11822336 | 118223 | 1194436
15 | Esperia Energy Group | Nicosia | 7.2 | Nicosia1 | ESP-2028 | Esperia Tseri | 7 | 20 | 7.2 | 4 | 1 | 5 |  |  | 2001736 |  |  |  | 7000 | 11800 |  | 9800 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 2335.16 | 2468.1 | 3967.95 | 1600 | 47513 | 40000 | 0 | 0 |  |  | 0 | 94671.21 | 2314570.02 | 115728.5 | 2559071.45 | 127953.57 |  | G2_ESP | 9 | 47513 | 30000 | 5455 | 82968 | 4148.4 | ✅ Feb 16 Update | 115589 |  | 2314570.02 | 244501.43 | 9.55 | 13% | 120683 | 2413660 | 0.12398 |  | 2301996 | 50945 | 68385 | 5922378 | 6692287 | 111538 | 689167
16 | Esperia Energy Group | Nicosia | 2.75 | Nicosia2 | ESP-2028 | Esperia Tseri 2a | 2.5 | 7.5 | 2.75 | 2 | 1 | 3 |  |  | 871307 |  |  |  | 5000 | 7080 |  | 3500 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 15000 | 0 | 0 |  |  | 0 | 53537.91 | 1055094.03 | 140679.2 | 1159991.35 | 154665.51 |  | G2_ESP | 9 | 33374 | 15000 | 5455 | 53829 | 7177.2 | ✅ Feb 16 Update | 135560 |  | 1055094.03 | 104897.32 | 9.04 | 13% | 146061 | 1095457.5 | 0.12731 |  | 1002003 | 35972 | 53409 | 2421326 | 2736098 | 136805 | 346802
17 | Esperia Energy Group | Nicosia | 8 | Nicosia3 | ESP-2028 | Esperia Tseri 2b | 7.5 | 25 | 8 | 5 | 2 | 7 |  |  | 2476649 |  |  |  | 9000 | 16520 |  | 10500 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 3382.09 | 3272.59 | 5555.13 | 1600 | 54583 | 50000 | 0 | 0 |  |  | 0 | 122229.81 | 2859896.41 | 114395.86 | 3169127.93 | 126765.12 |  | G2_ESP | 9 | 54583 | 30000 | 5455 | 90038 | 3601.52 | ✅ Feb 16 Update | 115589 |  | 2859896.41 | 309231.52 | 9.76 | 13% | 118015 | 2950375 | 0.11505 |  | 2848146 | 67183 | 75873 | 1091384 | 1233264 | 164435 | 152989
18 | Esperia Energy Group | Nicosia | 6.3 | Nicosia4 | ESP-2028 | Esperia Tseri 2c | 6 | 20 | 6.3 | 4 | 1 | 5 |  |  | 1907319 |  |  |  | 7000 | 11800 |  | 8400 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 2335.16 | 2468.1 | 3967.95 | 1600 | 47513 | 40000 | 0 | 0 |  |  | 0 | 93271.21 | 2314570.02 | 115728.5 | 2559071.45 | 127953.57 |  | G2_ESP | 9 | 47513 | 30000 | 5455 | 82968 | 4148.4 | ✅ Feb 16 Update | 115589 |  | 2314570.02 | 244501.43 | 9.55 | 13% | 114051 | 2281020 | 0.11504 |  | 2193417 | 49335 | 68385 | 2991202 | 3380058 | 135202 | 429694
19 | Esperia Energy Group | Nicosia | 4.75 | Nicosia5 | ESP-2028 | Esperia Tseri 3 | 4.5 | 15 | 4.75 | 3 | 1 | 4 |  |  | 1562533 |  |  |  | 7000 | 11800 |  | 6300 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 1905.75 | 2134.45 | 3174.36 | 1600 | 40444 | 30000 | 0 | 0 |  |  | 0 | 86314.56 | 1824719.46 | 121647.96 | 2008826.72 | 133921.78 |  | G2_ESP | 9 | 40444 | 30000 | 5455 | 75899 | 5059.93 | ✅ Feb 16 Update | 130792 |  | 1824719.46 | 184107.26 | 9.16 | 13% | 125877 | 1888155 | 0.11505 |  | 1796913 | 54625 | 60897 | 2311137 | 2611585 | 130579 | 330562
11 | Lampros Andreadis | Limassol | 1.5 | Limassol2 | CLS | Classone Solar Breeze | 1.51 | 5 | 1.5 | 1 | 1 | 2 |  |  | 585976 |  |  |  | 4000 | 4720 |  | 2114 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 10000 | 0 | 0 |  |  | 0 | 42235.26 | 786343.67 | 157268.73 | 795443.4 | 159088.68 |  | STANDALONE | 2 | 26304 | 15000 | 60000 | 101304 | 20260.8 | ✅ Feb 16 Update | 165431 |  | 786343.67 | 9099.73 | 1.14 | 13% | 154079 | 770395 | 0.15121 |  | 673872 | 30514 | 69254 | 1912435 | 2161052 | 144070 | 272901
12 | Lampros Andreadis | Limassol | 3 | Limassol3 | CLS | Classone Solar Garden | 3.29 | 10 | 3 | 2 | 1 | 3 |  |  | 1007809 |  |  |  | 5000 | 7080 |  | 4606 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 20000 | 0 | 0 |  |  | 0 | 59643.91 | 1210565.86 | 121056.59 | 1321976.2 | 132197.62 |  | STANDALONE | 2 | 33374 | 30000 | 0 | 63374 | 6337.4 | ✅ Feb 16 Update | 136106 |  | 1210565.86 | 111410.35 | 8.43 | 13% | 126214 | 1262140 | 0.13712 |  | 1158980 | 37244 | 76742 | 4551735 | 5143461 | 128587 | 543861
45 | A Kerasi | Paphos | 3.15 | Paphos1 | PAP | Paphos 1 | 2.5 | 7.5 | 3.15 | 2 | 1 | 3 |  |  | 871307 |  |  |  | 5000 | 7080 |  | 3500 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 15000 | 0 | 0 |  |  | 0 | 53537.91 | 1109039.03 | 147871.87 | 1159301.69 | 154573.56 |  | STANDALONE | 3 | 33374 | 15000 | 60000 | 108374 | 14449.87 | ✅ Feb 16 Update | 135560 |  | 1109039.03 | 50262.66 | 4.34 | 13% | 147998 | 1109985 | 0.14281 |  | 1002003 | 35972 | 66742 | 4551735 | 5143461 | 128587 | 543861
46 | A Kerasi | Paphos | 3 | Paphos2 | PAP | Paphos 2 | 2.5 | 7.5 | 3 | 2 | 1 | 3 |  |  | 871307 |  |  |  | 5000 | 7080 |  | 3500 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1476.34 | 1800.8 | 2380.77 | 1600 | 33374 | 15000 | 0 | 0 |  |  | 0 | 53537.91 | 1109039.03 | 147871.87 | 1159301.69 | 154573.56 |  | STANDALONE | 3 | 33374 | 15000 | 60000 | 108374 | 14449.87 | ✅ Feb 16 Update | 135560 |  | 1109039.03 | 50262.66 | 4.34 | 13% | 147998 | 1109985 | 0.14281 |  | 1002003 | 35972 | 66742 | 4551735 | 5143461 | 128587 | 543861
47 | A Kerasi | Paphos | 1.5 | Paphos3 | PAP | Paphos 3 | 1.5 | 5 | 1.5 | 1 | 1 | 2 |  |  | 541046 |  |  |  | 4000 | 4720 |  | 2100 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 10000 | 0 | 0 |  |  | 0 | 42221.26 | 740514.8 | 148102.96 | 742766.53 | 148553.31 |  | STANDALONE | 3 | 26304 | 15000 | 60000 | 101304 | 20260.8 | ✅ Feb 16 Update | 165431 |  | 740514.8 | 2251.74 | 0.3 | 13% | 141661 | 708305 | 0.14025 |  | 622203 | 30498 | 59254 | 4551735 | 5143461 | 128587 | 543861
13 | Ioannis Karis | Limassol | 7.7 | Limassol4 | MSP | My Sun Park | 7.7 | 25 | 7.7 | 5 | 2 | 7 |  |  | 2523652 |  |  |  | 9000 | 16520 |  | 10780 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 3382.09 | 3272.59 | 5555.13 | 1600 | 54583 | 50000 | 0 | 0 |  |  | 0 | 122509.81 | 2899287.02 | 115971.48 | 3220674.61 | 128826.98 |  | STANDALONE | 1 | 54583 | 30000 | 0 | 84583 | 3383.32 | ✅ Feb 16 Update | 115589 |  | 2899287.02 | 321387.59 | 9.98 | 13% | 123885 | 3097125 | 0.14317 |  | 2902200 | 67505 | 129206 | 4551735 | 5143461 | 128587 | 543861
7 | Timotheos Timotheou | Famagusta | 1 | Famagusta7 | LT | L&T Res Systems | 1 | 4 | 1 | 1 | 1 | 2 |  |  | 509419 |  |  |  | 4000 | 4720 |  | 1400 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 8000 | 0 | 0 |  |  | 0 | 39521.26 | 652668.78 | 163167.2 | 705395.26 | 176348.81 |  | G3_TIM | 5 | 26304 | 15000 | 6667 | 47971 | 11992.75 | ✅ Feb 16 Update | 165431 |  | 652668.78 | 52726.47 | 7.47 | 13% | 165684 | 662736 | 0.11504 |  | 585832 | 29693 | 51254 | 3054394 | 3451465 | 143811 | 437780
6 | Timotheos Timotheou | Famagusta | 1.5 | Famagusta6 | LT | L&T Solar Power | 1.5 | 5 | 1.5 | 1 | 1 | 2 |  |  | 585976 |  |  |  | 4000 | 4720 |  | 2100 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 10000 | 0 | 0 |  |  | 0 | 42221.26 | 734796.67 | 146959.33 | 797496.28 | 159499.26 |  | G3_TIM | 5 | 26304 | 15000 | 6667 | 47971 | 9594.2 | ✅ Feb 16 Update | 165431 |  | 734796.67 | 62699.61 | 7.86 | 13% | 150007 | 750035 | 0.11504 |  | 673872 | 30498 | 51254 | 1955573 | 2209797 | 147320 | 247917
14 | Timotheos Timotheou | Limassol | 5 | Limassol5 | LT | L&T Sun Energy | 5 | 15 | 5 | 3 | 1 | 4 |  |  | 1592098 |  |  |  | 7000 | 11800 |  | 7000 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 1905.75 | 2134.45 | 3174.36 | 1600 | 40444 | 30000 | 0 | 0 |  |  | 0 | 87014.56 | 1854905.15 | 123660.34 | 2042129.81 | 136141.99 |  | G3_TIM | 5 | 40444 | 30000 | 6667 | 77111 | 5140.73 | ✅ Feb 16 Update | 130792 |  | 1854905.15 | 187224.67 | 9.17 | 13% | 130792 | 1961880 | 0.13016 |  | 1830913 | 55430 | 66230 | 758624 | 857245 | 171449 | 103818
44 | Timotheos Timotheou | Nicosia | 8 | Nicosia30 | AGM | AGM Lightpower | 8 | 24 | 8 | 5 | 2 | 7 |  |  | 2523652 |  |  |  | 9000 | 16520 |  | 11200 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 3382.09 | 3272.59 | 5555.13 | 1600 | 54583 | 48000 | 0 | 0 |  |  | 0 | 120929.81 | 2908574.02 | 121190.58 | 3225984.95 | 134416.04 |  | G3_TIM | 4 | 54583 | 30000 | 6667 | 91250 | 3802.08 | ✅ Feb 16 Update | 115589 |  | 2908574.02 | 317410.93 | 9.84 | 13% | 127022 | 3048528 | 0.12516 |  | 2902200 | 67988 | 84206 | 669779 | 756850 | 189212 | 90723
39 | Timotheos Timotheou | Nicosia | 5 | Nicosia25 | AGM | AGM Sunfield 1 | 5 | 15 | 5 | 3 | 1 | 4 |  |  | 1592098 |  |  |  | 7000 | 11800 |  | 7000 | 7000 | 4400 | 6000 | 3000 | 2000 |  | 1905.75 | 2134.45 | 3174.36 | 1600 | 40444 | 30000 | 0 | 0 |  |  | 0 | 87014.56 | 1857305.15 | 123820.34 | 2044888.43 | 136325.9 |  | G3_TIM | 4 | 40444 | 30000 | 6667 | 77111 | 5140.73 | ✅ Feb 16 Update | 130792 |  | 1857305.15 | 187583.29 | 9.17 | 13% | 130792 | 1961880 | 0.12863 |  | 1830913 | 55430 | 69230 | 666779 | 753460 | 188365 | 90723
40 | Timotheos Timotheou | Nicosia | 4.5 | Nicosia26 | AGM | AGM Sunfield 2 | 1.5 | 5 | 4.5 | 1 | 1 | 2 |  |  | 585976 |  |  |  | 4000 | 4720 |  | 2100 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 10000 | 0 | 0 |  |  | 0 | 42221.26 | 734196.67 | 146839.33 | 796806.62 | 159361.32 |  | G3_TIM | 4 | 26304 | 15000 | 6667 | 47971 | 9594.2 | ✅ Feb 16 Update | 165431 |  | 734196.67 | 62609.95 | 7.86 | 13% | 150685 | 753425 | 0.11504 |  | 673872 | 30498 | 54254 | 755624 | 853855 | 170771 | 103818
41 | Timotheos Timotheou | Nicosia | 1 | Nicosia27 | AGM | AGM Sunfield 3 | 1 | 4 | 1 | 1 | 1 | 2 |  |  | 509419 |  |  |  | 4000 | 4720 |  | 1400 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 8000 | 0 | 0 |  |  | 0 | 39521.26 | 652068.78 | 163017.2 | 704705.6 | 176176.4 |  | G3_TIM | 4 | 26304 | 15000 | 6667 | 47971 | 11992.75 | ✅ Feb 16 Update | 165431 |  | 652068.78 | 52636.82 | 7.47 | 13% | 166532 | 666128 | 0.11505 |  | 585832 | 29693 | 54254 | 1952573 | 2206407 | 147094 | 244527
42 | Timotheos Timotheou | Nicosia | 1.5 | Nicosia28 | LT | L&T Energia | 1.5 | 5 | 1.5 | 1 | 1 | 2 |  |  | 585976 |  |  |  | 4000 | 4720 |  | 2100 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 10000 | 0 | 0 |  |  | 0 | 42221.26 | 734196.67 | 146839.33 | 796806.62 | 159361.32 |  | G3_TIM | 5 | 26304 | 15000 | 6667 | 47971 | 9594.2 | ✅ Feb 16 Update | 165431 |  | 734196.67 | 62609.95 | 7.86 | 13% | 150007 | 750035 | 0.11504 |  | 673872 | 30498 | 51254 | 755624 | 853855 | 170771 | 103818
43 | Timotheos Timotheou | Nicosia | 1 | Nicosia29 | LT | L&T PV Tech | 1 | 4 | 1 | 1 | 1 | 2 |  |  | 509419 |  |  |  | 4000 | 4720 |  | 1400 | 3500 | 2200 | 5000 | 3000 | 2000 |  | 1046.93 | 1467.15 | 1587.18 | 1600 | 26304 | 8000 | 0 | 0 |  |  | 0 | 39521.26 | 652068.78 | 163017.2 | 704705.6 | 176176.4 |  | G3_TIM | 5 | 26304 | 15000 | 6667 | 47971 | 11992.75 | ✅ Feb 16 Update | 165431 |  | 652068.78 | 52636.82 | 7.47 | 13% | 165684 | 662736 | 0.11504 |  | 585832 | 29693 | 51254 | 666779 | 753460 | 188365 | 90723
Average |  |  |  | TOTALS |  | TOTALS |  |  |  | Average | Average | Average | Average | Average |  | Average | Average | Average | Average | Average |  | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average | 1600 |  | Average | Average | Average | Average | Average | Average |  |  | Average |  | Average
Total |  |  |  | DATA VERIFICATION STATUS |  |  | Total | Total |  | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total |  | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total |  | Total | Total | Total | Total | Total | Total mvh | Total anual service | Total | Margin | Total
VERIFIED: 42 parks (Voltus Quote + PV Plants List)
UNVERIFIED: 5 parks (2028 Esperia - Estimates)
LEGEND: |  |  |  | PURPLE=Info ¦ DARK BLUE=CIF/Equipment ¦ BLUE=Subcontractor Adders ¦ GREEN=EMS/SCADA ¦ GOLD=Dino Pricing ¦ ORANGE=Target ¦ NAVY BLUE=Individual Order (+15%)
Price Types: |  |  |  | DINO LOCKED = Fixed price ¦ 13% MARGIN = Re-priced at 13% ¦ 9% MARGIN = Re-priced at 9% ¦ NEW ABIO = New park NEEDS VERIFICATION
Note: |  |  |  | RED status cells = NEEDS VERIFICATION ¦ YELLOW data cells = ESTIMATED costs ¦ ALL PRICING MUST REFERENCE THIS SPREADSHEET AS SINGLE SOURCE OF TRUTH
- CIF prices: Linyang Quotation Jan 2026
- SCADA Global: EUR 60,000 per group (allocated by parks in group)
- SCADA Local: EUR 15,000 per park

## Verify
No | Checked
MV interface works (physical connection)
MV outage planning + method statement + switching plan with the DSO / site owner.
Interruption works to move / re-terminate the existing PV MV feeder into the NEW RMU (the “existing MV cable” shown).
Any new MV cable sections/joints if the existing cable length/routing doesn’t reach the NEW RMU cleanly (straight-through joints, sealing ends, link boxes if required).
MV terminations, glands, earthing of screens, and identification/labels.
NEW RMU bays and protection for the PV feeder
Provide the RMU way (bay) that feeds the existing PV park: typically CB or fused switch (as per utility requirement), with CTs (and VTs if required by the protection scheme).
Protection relays/settings for the PV feeder (overcurrent/earth fault at minimum; directionality if required by the network).
Protection coordination study covering: PV feeder protection, transformer feeder protection, and upstream DSO protection (this is usually a hard requirement to get approval).
Metering and compliance interface (often underestimated)
Confirm whether the existing revenue meter / check meter stays where it is or must be reworked due to the new node. If the metering point changes, you may need new CT/VT metering cores and meter panel wiring.
Any DSO-required interlocks (trip signals, remote open, emergency stop interface) and status indications (CB open/close, protection trip, earth switch position).
Controls / EMS integration with existing PV (only if required by the project’s operating philosophy)
If the EMS will control PV curtailment or coordinate PV+BESS export limits, you need a data interface to the PV plant controller/inverters (Modbus TCP/RTU or vendor API), plus a defined control responsibility matrix.
Communications backbone: fibre/Ethernet from control room/EMS to the RMU/protection and (if needed) to the PV plant controller.
Earthing and lightning bonding continuity
Verify the earthing grid continuity between the new RMU, existing PV substation, and the BESS equipment; add earth conductors/earth pits as needed.
MV screen bonding design (single-point vs both-ends) consistent with fault levels and touch/step limits.
Testing, commissioning, documentation (for the PV interface portion)
MV cable tests (VLF/PD if specified), phasing checks, relay secondary injection, functional trip tests.
Updated as-built SLDs, cable schedules, protection setting files, test reports.
Commissioning procedure proving the existing PV operates correctly after reconfiguration (before energising BESS in parallel).