L	LIGHTHIEF

Energy Storage Solutions | Cyprus

Ref: LCY-RFI-VOLTUS-2026-002

Version: 1.0

Date: 10 February 2026

Priority: HIGH

REQUEST FOR INFORMATION

EMS / SCADA Pricing Update & Bill of Materials Confirmation

Revised Group Structure — Cyprus BESS Portfolio (51 Parks / ~912 MWh)

# PURPOSE

Dear Voltus Team,

Following our original RFI (LCY-RFI-EMS-2026-001, 2 February 2026) and the Voltus pricing quote received in January 2026, we have finalized the commercial and operational structure for the Cyprus BESS portfolio. This RFI requests:

- Updated pricing based on a revised 3-group structure (down from 6+ groups)

- Confirmation of Bill of Materials (BoM) per site — specifically WAGO hardware included in your quote

- Scope boundary clarification — what Lighthief (EPC) must procure vs. what Voltus supplies

- Confirmation of OEM-shipped items already included in Linyang's delivery that interface with EMS

Response requested by: 21 February 2026

Please provide updated pricing and BoM confirmation at your earliest convenience. We are finalizing EPC contracts with clients and need to confirm all-in turnkey costs.

Standalone pricing for 6 parks outside the main groups

# REVISED COMMERCIAL STRUCTURE

  - Stakeholder Roles

| Entity | Role | Responsibilities |
| --- | --- | --- |
| Lighthief Cyprus Ltd | EPC Contractor, Installer, O&M Provider, Linyang Distributor | Turnkey BESS EPC delivery (incl. EMS/SCADA) Exclusive distributor for Linyang in Cyprus Master EMS & SCADA management across portfolio Long-term O&M and BESS service partner Procures and installs all EMS/SCADA hardware & software |
| Voltus | EMS/SCADA Provider | EMS software, WAGO hardware, SCADA platform PPC + RTU functionality (integrated in WAGO controller) Remote configuration, commissioning support, training |
| Linyang / Kehua | OEM Equipment Supplier | Battery containers (5 MWh LFP), PCS (Kehua BCS-C- HUD), MV Skids BMS (3-level: BMU/BCMU/BAMS), RTU (confirmed included) Installation & OEM commissioning Spares stock (see Section 5) |
| ABIO | Aggregator (Group 1) | Market aggregator for ABIO Power parks |
| Synenergia | Aggregator (Group 2) | Market aggregator for Esperia Energy Group parks |

Per-Site Architecture (confirmed by Linyang OEM — Kamil Tyburski, Feb 2026):

Cyprus DSO (EAC)

|

| IEC 60870-5-104

|

[WAGO PFC200] — PPC + RTU + IEC-104 gateway (Voltus supply)

|

|--- Modbus TCP ---> Kehua PCS (BCS-C-HUD) — accepts external setpoints

|--- Modbus TCP ---> Linyang BMS (BAMS) — battery monitoring

|--- Voltus EMS Software — dispatch, optimization, grid services

|

Voltus SCADA Local ---> Voltus SCADA Global (per group, on-premise)

Confirmed System Architecture

Key confirmation: No separate PPC hardware required. WAGO controller integrated with PPC + RTU functions. Kehua PCS accepts direct setpoint commands via Modbus TCP.

Abbreviation Key

| Group & Park Abbreviations |  |  |  |
| --- | --- | --- | --- |
| Code | Full Name | Code | Full Name |
| ABIO | ABIO Power (Client / Group 1) | ESP | Esperia Energy Group (Client / Group 2) |
| TIM | Timotheos Timotheou (Client / Group 3) | CLS | Classone (Lampros Andreadis) |
| PAP | Paphos (A Kerasi) | MSP | My Sun Park (Ioannis Karis) |
| ABIO Sub-groups |  |  |  |
| GRD | Greendorado | DIA | Dianary |
| ELE | ELESTORE | EAS | Easy Power |
| POL | Polemi | POT | Potamia |
| REN | Renergetic | SOL | Solarity |
| SLT | Solartech | WAN | Waneron |
| ASZ | Agios Sozomenos |  |  |
| ESP Sub-groups |  |  |  |
| GAL | Galascope | ESP-28 | Esperia Tseri (2028 phase) |
| TIM Sub-groups |  |  |  |
| LT | L&T (various entities) | AGM | AGM (various entities) |

  - Revised Group Structure (3 Groups + 6 Standalone)

Change from previous quote: The original Voltus quote had 15 groups, later consolidated to 6. We have now finalized at 3 main groups + 6 standalone parks. This reduces SCADA Global instances from 6 to 3 for the main groups, with 6 standalone parks priced individually.

G1: ABIO — Aggregator: ABIO — 25 Parks

| Code | Park | MW | MWh | Cnt | MV | Batt | Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GRD-AV | Greendorado Agrivoltaic | 0.75 | 3 | 2 | 1 | 1 | NEW |
| GRD-L1 | Greendorado Larnaca 1 | 1.25 | 5 | 2 | 1 | 1 | VER |
| GRD-L2 | Greendorado Larnaca 2 | 1.0 | 5 | 2 | 1 | 1 | VER |

| GRD-1 | Greendorado 1 | 1.8 | 8 | 3 | 1 | 2 | VER |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ASZ | , | 6.0 | 25 | 6 | 1 | 5 | NEW |
| DIA-1 | Dianary 1 | 2.5 | 10 | 3 | 1 | 2 | VER |
| DIA-2 | Dianary 2 | 2.5 | 10 | 3 | 1 | 2 | VER |
| DIA-3 | Dianary 3 | 8.0 | 35 | 9 | 2 | 7 | VER |
| ELE-1 | ELESTORE 1 | 12.0 | 40 | 10 | 2 | 8 | VER |
| ELE-2 | ELESTORE 2 | 12.0 | 40 | 10 | 2 | 8 | VER |
| ELE-3 | ELESTORE 3 | 12.0 | 40 | 10 | 2 | 8 | VER |
| ELE-4 | ELESTORE 4 | 12.0 | 40 | 10 | 2 | 8 | VER |
| ELE-5 | ELESTORE 5 | 12.0 | 40 | 10 | 2 | 8 | VER |
| EAS-1 | Easy Power 1 | 5.0 | 10 | 3 | 1 | 2 | VER |
| EAS-2 | Easy Power 2 | 4.5 | 10 | 3 | 1 | 2 | VER |
| EAS-3 | Easy Power 3 | 5.0 | 10 | 5 | 2 | 3 | VER |
| EAS-4 | Easy Power 4 | 1.8 | 8 | 3 | 1 | 2 | VER |
| POL | Polemi8 | 1.25 | 10 | 4 | 1 | 3 | VER |
| POT-151 | Potamia p151 | 1.25 | 10 | 4 | 1 | 3 | VER |
| POT-208 | Potamia p208 | 4.5 | 20 | 8 | 2 | 6 | VER |
| REN-1 | Renergetic | 5.0 | 10 | 3 | 1 | 2 | VER |
| REN-2 | Renergetic 2 | 2.4 | 10 | 3 | 1 | 2 | NEW |
| SOL | Solarity | 5.0 | 10 | 3 | 1 | 2 | VER |
| SLT-3X | Solartech 3 Ext. | 2.5 | 10 | 3 | 1 | 2 | NEW |
| WAN | Waneron | 3.0 | 11.28 | 3 | 1 | 2 | VER |
|  | G1 TOTAL | 125.0 | 430.3 | 125 | 33 | 92 | 1 SCADA Gl. |

G2: ESP — Aggregator: Synenergia — 11 Parks

| Code | Park | MW | MWh | Cnt | MV | Batt | Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ESP-F1 | Esperia Famagusta | 6.5 | 20 | 5 | 1 | 4 | VER |
| ESP-F2 | Esperia Famagusta 2 | 5.0 | 20 | 5 | 1 | 4 | VER |

| ESP-FR | Esperia Frenaros | 25.0 | 100 | 23 | 3 | 20 | VER |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ESP-LIM | Esperia Limassol | 8.0 | 60 | 14 | 2 | 12 | VER |
| GAL-1 | Galascope 1 | 5.0 | 15 | 5 | 2 | 3 | VER |
| GAL-2 | Galascope 2 | 2.5 | 8 | 3 | 1 | 2 | VER |
| ESP-T1 | Esperia Tseri | 7.0 | 20 | 5 | 1 | 4 | 2028 |
| ESP-T2a | Esperia Tseri 2a | 2.5 | 7.5 | 3 | 1 | 2 | 2028 |
| ESP-T2b | Esperia Tseri 2b | 7.5 | 25 | 7 | 2 | 5 | 2028 |
| ESP-T2c | Esperia Tseri 2c | 6.0 | 20 | 5 | 1 | 4 | 2028 |
| ESP-T3 | Esperia Tseri 3 | 4.5 | 15 | 4 | 1 | 3 | 2028 |
|  | G2 TOTAL | 79.5 | 310.5 | 79 | 16 | 63 | 1 SCADA Gl. |

G3: TIM — 9 Parks

| Code | Park | MW | MWh | Cnt | MV | Batt | Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| LT-RS | L&T Res Systems | 1.0 | 4 | 2 | 1 | 1 | VER |
| LT-SP | L&T Solar Power | 1.5 | 5 | 2 | 1 | 1 | VER |
| LT-SE | L&T Sun Energy | 5.0 | 15 | 4 | 1 | 3 | VER |
| LT-EN | L&T Energia | 1.5 | 5 | 2 | 1 | 1 | VER |
| LT-PV | L&T PV Tech | 1.0 | 4 | 2 | 1 | 1 | VER |
| AGM-LP | AGM Lightpower | 8.0 | 24 | 7 | 2 | 5 | VER |
| AGM-SF1 | AGM Sunfield 1 | 5.0 | 15 | 4 | 1 | 3 | VER |
| AGM-SF2 | AGM Sunfield 2 | 1.5 | 5 | 2 | 1 | 1 | VER |
| AGM-SF3 | AGM Sunfield 3 | 1.0 | 4 | 2 | 1 | 1 | VER |
|  | G3 TOTAL | 25.5 | 81.0 | 27 | 10 | 17 | 1 SCADA Gl. |

Standalone (Individual SCADA Global Each)

| Code | Park | Owner | MW | MWh | Cnt | MV | Batt |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CLS-SB | Classone Solar Breeze | L. Andreadis | 1.51 | 5 | 2 | 1 | 1 |
| CLS-SG | Classone Solar Garden | L. Andreadis | 3.29 | 10 | 3 | 1 | 2 |
| PAP-1 | Paphos 1 | A Kerasi | 2.5 | 7.5 | 3 | 1 | 2 |

| PAP-2 | Paphos 2 | A Kerasi | 2.5 | 7.5 | 3 | 1 | 2 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PAP-3 | Paphos 3 | A Kerasi | 1.5 | 5 | 2 | 1 | 1 |
| MSP | My Sun Park | I. Karis | 7.7 | 25 | 7 | 2 | 5 |
|  | STANDALONE TOTAL |  | 19.0 | 60.0 | 20 | 7 | 13 |

  - Portfolio Summary

| Group | Parks | MW | MWh | Cnt | SCADA Gl. |
| --- | --- | --- | --- | --- | --- |
| G1: ABIO | 25 | 125.0 | 430.3 | 125 | 1 |
| G2: ESP | 11 | 79.5 | 310.5 | 79 | 1 |
| G3: TIM | 9 | 25.5 | 81.0 | 27 | 1 |
| Standalone (6 parks) | 6 | 19.0 | 60.0 | 20 | 6 (individual) |
| TOTAL | 51 | 249.0 | 881.8 | 251 | 9 |

# PRICING UPDATE REQUEST

Based on the revised 3-group + 6 standalone structure, please provide updated pricing for the following:

  - Group Pricing (SCADA Global shared across group)

| Cost Component | G1: ABIO (25) | G2: ESP (11) | G3: TIM (9) |
| --- | --- | --- | --- |
| EMS per park (System + Hardware) | 549 345 | 327 762 | 140 059 |
| Remote Configuration & Preparation (per park) | 344 280/25 = 13 771 | 188 232/11= 17 112 | 100 728/9=11 192 |
| On-site Installation + Training (per park) | 237 650 / 25 = 9 506 | 150 732 | 52 508 |
| SCADA Local (per park) | Basic =15 000 (Advance =30 000 more 10MWh) | Basic =15 000 (Advance =30 000 more 10MWh) | Basic =15 000 (Advance =30 000 more 10MWh) |
| SCADA Global (one-time, per group) | 60 000 | 60 000 | 60 000 |
| SCADA Local Maintenance (per park/year) | 3 000 | 3 000 | 3 000 |
| SCADA Global Maintenance (per group/year) | 12 000 | 12 000 | 12 000 |

  - Standalone Park Pricing (individual SCADA Global per park)

| Park | MW/MWh | EMS (System + HW) | SCADA Local | SCADA Global | Total |
| --- | --- | --- | --- | --- | --- |
| CLS-SB | 1.51/5 | 12 380 | 15 000 | - |  |
| CLS-SG | 3.29/10 | 15 960 | 30 000 | - |  |
| PAP-1 | 2.5/7.5 | 15 960 | 15 000 | - |  |
| PAP-2 | 2.5/7.5 | 15 960 | 15 000 | - |  |
| PAP-3 | 1.5/5 | 12 380 | 15 000 | - |  |
| MSP | 7.7/25 | 26 699 | 30 000 | - |  |

  - Volume Discount

| Question | Response |
| --- | --- |
| Are the January 2026 quoted prices still valid, or have they been updated? | update with notes on changes to parameter installation and new update scada |
| Is there an additional volume discount for the full 51-park portfolio ordered together? | yes there is an additional discount of 5% |
| Can standalone parks receive discounted SCADA Global pricing if ordered as part of the portfolio? | Yes, there is an additional 5% discount and a one free global scada for all installations and one service scada (you get 2 free scada) |
| Is there a discount for multi-year SCADA maintenance commitment (e.g. 5-year)? | Yes, there is a discount. We will provide ten discounts after determining the final number of SCADs in global |

# BILL OF MATERIALS (BoM) — CONFIRMATION REQUIRED

Critical: Lighthief delivers turnkey EPC including EMS/SCADA to the end client. We need to confirm exactly what hardware is included in Voltus pricing vs. what Lighthief must procure separately. Please confirm or correct the following understanding.

WAGO Hardware — Included in Voltus "System + Hardware"?

| Component | Our Understanding | Voltus Confirmation |
| --- | --- | --- |
| WAGO PFC200 PLC Controller (PPC + RTU + IEC-104 combined) | Included in Voltus | Yes |
| WAGO I/O Modules (750 series) (Digital/analog I/O, power measurement) | Included in Voltus | Yes |
| Energy Meters (Grid-side, BESS-side power metering) | Confirm | no |
| Network Switch (managed) | Confirm | no |
| Industrial Router / VPN Firewall | Confirm | no |
| 4G/LTE SIM Router (Remote connectivity) | Confirm | no |
| Control Cabinet / Enclosure (DIN-rail housing for WAGO + network) | Confirm | no |
| UPS for Controls (Backup power for WAGO/network) | Confirm | no |
| EMS Software License | Included in Voltus | Yes |
| SCADA Local Software | Included in Voltus | Yes |

  - Items to be Procured by Lighthief (EPC)?

Please confirm if any of the following must be ordered separately by Lighthief:

| Item | Included by Voltus? | Lighthief to Procure? |
| --- | --- | --- |
| SIM cards for 4G/LTE connectivity | no |  |
| Ethernet/fibre cabling (site internal) | no |  |
| GPS antenna (for time sync) | no |  |
| Revenue meter (if separate from EMS metering) | no |  |

| CT/VT transducers (current/voltage transformers) | No |  |
| --- | --- | --- |
| SCADA Global server hardware (on-premise) | No |  |
| Any other items not listed above |  |  |

Please provide a detailed Bill of Materials for each site size category: Small site (1-3 MW / 1-2 PCS units / 1 MV Skid)

Medium site (4-8 MW / 3-6 PCS units / 1-2 MV Skids)

Large site (10-15 MW / 8-10 PCS units / 2 MV Skids)

XL site (20-30 MW / 15-20 PCS units / 2-3 MV Skids)

For each, please list: part number, description, quantity, and whether it is included in the Voltus price or to be procured by Lighthief.

Detailed BoM Request

# OEM-SHIPPED ITEMS (Linyang / Kehua) — Interface with EMS

The following items are confirmed as shipped by Linyang OEM as part of the BESS supply order. Please confirm compatibility and whether any of these overlap with or replace Voltus-supplied components.

  - Linyang OEM Equipment (Relevant to EMS/SCADA)

| OEM Component | Details | Interface to EMS | Voltus Notes |
| --- | --- | --- | --- |
| RTU (Remote Terminal Unit) | Confirmed included in Linyang MV Skid scope | IEC 60870-5-104 | replace this |
| BMS (BAMS Level 3) | Linyang 3-level BMS: BMU/BCMU/BAMS | Modbus TCP, CAN, RS485 | Voltus reads from BAMS via Modbus TCP |
| Kehua PCS Controller | BCS-C-HUD series, accepts external setpoints | Modbus TCP | Voltus/WAGO sends P/Q setpoints via Modbus TCP |
| Auxiliary System & Comms Cabinet | Included in Linyang scope (details pending) | TBC | Does this contain any EMS-relevant hardware? |

Confirmed by Kamil Tyburski (Linyang) — February 2026 via WhatsApp: 3 pallets of PCS spares per PCS configuration (Kehua BCS-C-HUD)

~8 racks of Li-ion cell racks for replacement battery stock

~40 pallets total spares shipment with order

These spares are held by Lighthief as the BESS service partner. They include PCS control boards, IGBT modules, cooling fans, BMS components, DC contactors/fuses, and battery packs.

Linyang Confirmed Spares Stock (Shipped with Order)

  - Interface Confirmation Required

| Question | Response |
| --- | --- |
| Does the Linyang-supplied RTU need to remain active, or does the WAGO PFC200 fully replace the RTU function? | Voltus Wago replaces RTU |
| Are there any Linyang-supplied meters or sensors that Voltus EMS needs to read? | This depends on the project. You should read the grid connection point and the mv skid connection point. |
| Does Voltus require any specific firmware version or configuration on the Kehua PCS for Modbus TCP integration? | voltus only requires a firmware with the provided communication documentation |

| Does Voltus need access to the Linyang BMS Modbus register map? (We can provide this — document ref: WRDF-0I002-103) | yes |
| --- | --- |
| Does Voltus need the Kehua IEC-104 point list? (We can provide this — document ref: WRWF-0I002-06) | yes |

# LIGHTHIEF MASTER EMS/SCADA MANAGEMENT

As the portfolio-wide EPC and O&M provider, Lighthief requires master-level access and management capability across all 51 parks. Please confirm:

| Requirement | Response |
| --- | --- |
| Can Lighthief have a master SCADA dashboard across all 3 groups + standalone parks? | yes |
| Can Lighthief access all parks regardless of which group/aggregator they belong to? | yes |
| Is there a separate license/cost for a Lighthief master portal? | Master Lighthief will be free if all scads are ordered |
| Can Lighthief receive consolidated alarm/fault notifications for all parks? | yes |
| Can Lighthief generate portfolio-wide performance reports? | yes |
| Can aggregators (ABIO, Synenergia) have read-only access to their respective group's SCADA? | yes |

Please submit your response to:

Email: alexander.papacosta@lighthief.com

Subject: RFI Response - Voltus EMS/SCADA Update Feb 2026 (LCY-RFI-VOLTUS-2026-002)

Deadline: 21 February 2026

Deliverables requested:

- Updated pricing per Section 3 (3 groups + 6 standalone)

- Completed BoM confirmation per Section 4

- OEM interface confirmation per Section 5

- Master management confirmation per Section 6

- Detailed per-site BoM (part numbers, quantities) for each site size

RESPONSE INSTRUCTIONS

Lighthief Cyprus Ltd

28 October Avenue 249, Lophitis Business Center 1, Office 201

3035 Limassol, Cyprus

Email: alexander.papacosta@lighthief.com | Tel: +357 99 164 158

Document Reference: LCY-RFI-VOLTUS-2026-002 | Version 1.0 | 10 February 2026 Classification: CONFIDENTIAL — For Voltus Energy use only