## Options Comparison
SIA 3.2 MWp — EPC Build Options (Internal Analysis)
Lighthief Cyprus Ltd — Confidential — May 2026
Metric | Option A Fixed 15° | Option B Fixed 25°+Albedo | Option C SAT Tracker | Option D SAT+Albedo
TECHNICAL
Specific yield (kWh/kWp/yr) | 1650 | 1900 | 2100 | 2300
Annual gross production (MWh) | 5280 | 6080 | 6720 | 7360
Solar dispatched direct (MWh) | 2640 | 3040 | 3360 | 3680
BESS discharged (MWh) | 1991 | 2294 | 2535 | 2776
Permit amendment required | No | No | Yes | Yes
PV EPC — SELF-COST → CLIENT PRICE
PV EPC self-cost | 1469723 | 1522223 | 1710173 | 1736423
Lighthief markup (€100k/MW) | 320000 | 320000 | 320000 | 320000
PV EPC client price | 1789723 | 1842223 | 2030173 | 2056423
PV EPC rate (€/MWp) | 559288.4375 | 575694.6875 | 634429.0625 | 642632.1875
BESS EPC (10 MWh × €125k) | 1250000 | 1250000 | 1250000 | 1250000
TOTAL PROJECT CAPEX (100% EQUITY)
RTB acquisition (€550k/MW × 3.2) | 1760000 | 1760000 | 1760000 | 1760000
PV EPC client | 1789723 | 1842223 | 2030173 | 2056423
BESS EPC | 1250000 | 1250000 | 1250000 | 1250000
EAC grid works (prelim.) | 83842 | 83842 | 83842 | 83842
Commission reserve (4%) | 195343 | 197443 | 204961 | 206011
TOTAL CAPEX | 5078908 | 5133508 | 5328976 | 5356276
REVENUE & RETURNS (50% curtailment ¦ €195/MWh discharge ¦ CIT 12.5%)
Gross Y1 revenue | 760168 | 875605 | 967682 | 1059758
Y1 OPEX | 123795 | 124068 | 125045 | 125181
Y1 EBITDA | 560356 | 663976 | 745869 | 828601
Y1 FCF (post-tax) | 523976 | 614972 | 687803 | 760358
Cash yield Y1 | 10.32% | 11.98% | 12.91% | 14.2%
Simple payback (yrs) | 9.7 | 8.3 | 7.7 | 7
RECOMMENDATION
RECOMMENDED: Option B — Fixed Tilt 25° + White Albedo ¦ Yield: 1,900 kWh/kWp • Only €52k more than Option A for +15% annual yield (no permit amendment) • Option B + €220/MWh discharge + €500k/MW acquisition → payback 8.2yr (see 'Option B Scenarios' sheet)

## Option B — Scenarios
Option B: Fixed 25° + White Albedo — Sensitivity Scenarios
Showing impact of discharge price and acquisition cost on payback / cash yield
Metric | B1 — Baseline | B2 — Higher Disc. Price | B3 — Lower Acquisition | B4 — COMBINED ★
SCENARIO PARAMETERS
Discharge price (€/MWh) | 195 | 220 | 195 | 220
Acquisition (€/MW) | 550000 | 550000 | 500000 | 500000
RTB total cost | 1760000 | 1760000 | 1600000 | 1600000
REVENUE
Solar revenue Y1 | 428275 | 428275 | 428275 | 428275
BESS revenue Y1 | 447330 | 504680 | 447330 | 504680
GROSS Y1 REVENUE | 875605 | 932955 | 875605 | 932955
CAPEX
RTB acquisition | 1760000 | 1760000 | 1600000 | 1600000
PV EPC client (same all scenarios) | 1842223 | 1842223 | 1842223 | 1842223
BESS EPC | 1250000 | 1250000 | 1250000 | 1250000
Grid works | 83842 | 83842 | 83842 | 83842
Commission reserve 4% | 197443 | 197443 | 191043 | 191043
TOTAL CAPEX | 5133508 | 5133508 | 4967108 | 4967108
KEY RETURNS — COMPARISON
Y1 FCF (post-tax) | 614972 | 660136 | 614367 | 659531
Cash yield Y1 | 11.98% | 12.86% | 12.37% | 13.28%
Simple payback | 8.3 | 7.8 | 8.1 | 7.5
COMBINED SCENARIO B4 DETAIL
★ B4 COMBINED: €220/MWh discharge + €500k/MW acquisition Total CAPEX: €4,967,108 ¦ Y1 FCF: €659,531 ¦ Payback: 7.5 years €220/MWh is still well below April 2026 observed peak (>€340/MWh) €500k/MW vs €550k/MW = €160k concession — negotiable as part of EPC package deal

## Option B — Full Breakdown
Option B — Fixed 25° + White Albedo — Full EPC Breakdown
PV EPC SELF-COST ITEMS (Pricing sources: Trikkis Mar 2026, AE Solar, market)
Item | € ex VAT
Panels (4,961 × 645W × €0.112/W EXW) | 358383
Panel transport Rotterdam → Cyprus site | 34392
Inverters (9 × SUN2000-330KTL-H1, Trikkis pallet) | 65961
Inverter shipping + handling | 4000
DC cables + MC4 connectors (Trikkis wholesale) | 160000
AC LV cabling (inverter → MV skid) | 50000
AC MV cabling (22kV to grid) | 60000
MV transformer station + 22kV switchgear | 100000
SCADA hardware (Huawei Smart Logger 3000) | 12000
Earthing + grounding system | 20000
Lightning protection (SPD, LPS) | 15000
Fire suppression | 8000
CCTV + perimeter alarm | 20000
Fencing 800m × €10 Trikkis + installation | 22000
Commissioning + EAC grid connection test | 25000
Project management fee | 60000
Engineering + structural design | 25000
CAR construction insurance | 20000
Civil works (ground prep, piling, trenches, roads) | 100000
Mounting structure (Fixed Tilt 25° + White Albedo) | 265000
White albedo ground treatment (limestone/PVC) | 25000
Contingency (5%) | 72487
PV EPC SELF-COST | 1522223
Lighthief markup (€100k/MW × 3.2) | 320000
PV EPC CLIENT PRICE | 1842223
TOTAL CAPEX STACK
RTB acquisition (€550k/MW × 3.2) | 1760000
PV EPC (client price) | 1842223
BESS EPC (10 MWh × €125k) | 1250000
EAC grid infrastructure (preliminary) | 83842
Commission reserve (4%) | 197443
TOTAL CAPEX | 5133508
YEAR 1 P&L (€195/MWh discharge, 50% curtailment, CIT 12.5%)
Solar revenue (3,040 MWh × €141) | 428275
BESS revenue (2,294 MWh × €195) | 447330
Gross Y1 revenue | 875605
Aggregator fee (10%) | -87560
OPEX (O&M, LTSA, land, insurance, admin) | -124068
EBITDA | 663976
Cyprus CIT (12.5%) | -49004
FREE CASH FLOW Y1 | 614972

## Pricing Sources
Pricing Sources & Assumptions
PANELS | AE Solar 645W bifacial — €0.112/W EXW Rotterdam (user-quoted). 4,961 panels for 3.2 MWp.
INVERTERS | Trikkis CY Pricelist Mar 2026 — SUN2000-330KTL-H1 pallet price €7,329.01 (code 200354). 9 units.
FENCING | Trikkis Mar 2026 — code 400127: €10/m wholesale (1.5m incl. pillars 2m). Gate 400128: €300 ea.
DC CABLES | Trikkis Mar 2026 — 4mm²: €0.52/m, 6mm²: €0.76/m, 10mm²: €1.41/m wholesale.
MV TRANSFORMER | User range €80-120k. Modelled at €100k midpoint.
CIVIL WORKS | User range €90-110k. Modelled at €100k midpoint (Option A/B). +€30k for tracker options.
MOUNTING — FIXED 15° | Market estimate Cyprus commercial ground-mount, installed: €240k (€48/panel).
MOUNTING — FIXED 25° | €265k (slightly more steel + longer pile legs for 25° angle).
MOUNTING — SAT TRACKER | €424k installed (~€85/panel incl. motor drives, aluminium rails, concrete posts).
WHITE ALBEDO | Crushed limestone or PVC sheeting under panels: €25k for 3.2 MWp site.
BESS EPC | Lighthief rate €125k/MWh × 10 MWh.
RTB ACQUISITION | Seller asking price €550k/MW × 3.2 MW. Scenario B3/B4 tests €500k/MW.
EAC GRID WORKS | Preliminary estimate ref 498000141 — €83,842 ex VAT. NOT BINDING (changes after TES).
LIGHTHIEF MARKUP | €100k/MW flat per internal solarpark-epc.md → €320k on 3.2 MWp.
COMMISSION RESERVE | 4% of base CAPEX added as project management buffer.
DAM PRICES | TSOC Cyprus DAM sample Oct 2025–Feb 2026: solar (06-17h) €140.88/MWh, BESS discharge €195/MWh modelled. Apr 2026 observed >€340/MWh.
CURTAILMENT | 50% — operator-confirmed for this site. Galascope 2025 actual: 42.8%.
BESS CAPTURE RATE | 87.4% — calibrated against Galascope 365-day real model with overflow constraints.
RTE | 86.32% AC-AC full system including cabling losses.
CIT | 12.5% Cyprus statutory corporate income tax rate.
OPEX | LTSA Tier C €1,740/MWh/yr (portfolio-data.ts confirmed) + SCADA €5k + land €18k + insurance 0.5% CAPEX + admin €10k.