## Estimate — Relyz PV + BESS
Lighthief Cyprus — Investment Estimate ¦ Solar PV ~3.2 MWp + BESS Installation
Client: Relyz-PV ¦ Date: April 2026 ¦ Revision: 1.0 ¦ All prices in EUR (excl. VAT)
Item | Scope | Qty | Unit (€) | Line total (€)
SECTION A — Solar PV, ~3.2 MWp (string inverters, mounting, BOS, civils, commissioning)
1 | PV modules — AE Solar Meteor AE630CMER-132BDS 630W TopCon bifacial (GG), EXW Rotterdam | 5080 | 69.3 | 352044
2 | String inverters — Huawei SUN2000-115KTL-M2, 115 kWac, 10 MPPT (24 units → 2.76 MWac; DC/AC 1.16) | 24 | 4393.63 | 105447
2a | Plant controller — Huawei SmartLogger 3000A03EU | 1 | 1007.16 | 1007
3 | Ground-mount structure — Helios 1-pole 2×portrait complete system (2,540 tables) | 2540 | 48 | 121920
4 | DC cabling — PV field (~32 km, supply) | 32238 | 1.02 | 32883
5 | AC cabling — LV (~8 km, supply) | 8000 | 3.6 | 28800
6 | BOS — cable trays, connectors, clamps, conduits, enclosures | 1 | 30000 | 30000
7 | Main LV switchboard + SCADA interface | 1 | 54000 | 54000
8 | Earthing & lightning protection — PV array / inverter area | 1 | 18000 | 18000
9 | Fire detection & suppression — PV site | 1 | 33600 | 33600
10 | CCTV & perimeter security system | 1 | 21600 | 21600
11 | Civil works — levelling, access roads, hardstands, drainage | 1 | 78000 | 78000
12 | Commissioning, EAC energisation & handover documentation | 1 | 48000 | 48000
| Section A sub-total |  |  | 925301
SECTION B — BESS Installation scope, 1 MW / 4 MWh (client-supplied battery containers, PCS & MV skid hardware)
⚠ Battery hardware (containers, PCS, MV skid) is client-supplied / procured separately. This section covers civil foundation, logistics coordination, electrical interfaces, protection engineering, LPS/SPD/earthing and commissioning support only.
B1 | Civil works — reinforced concrete pads (2×20 ft containers + MV skid) | 1 | 62400 | 62400
B2 | Logistics — port handling, customs, heavy transport to site | 1 | 6828 | 6828
B3 | LV cabling & cable tray within BESS yard | 1 | 7800 | 7800
B4 | MV feeder cable + terminations (skid → point of interconnection) | 1 | 6840 | 6840
B5 | Protection engineering (relay settings, co-ordination study) | 1 | 6600 | 6600
B6 | Remote trip interface + UPS / auxiliary power supply | 1 | 6360 | 6360
B7 | Lightning protection (LPS), surge protection (SPD) & earthing system | 1 | 33600 | 33600
B8 | BESS commissioning support & acceptance testing (client equipment) | 1 | 21600 | 21600
| Section B sub-total |  |  | 152028
| TOTAL — Sections A + B (excl. VAT) |  |  | 1077329
Excluded from this estimate: • VAT (19% Cyprus) • MV/HV step-up transformer(s) and MV switchgear at the point of interconnection with the DSO grid • DSO grid-connection contribution / network extension works • EAC metering and protection relay hardware (relay hardware at POI) • Fencing (perimeter to plot boundary) unless explicitly agreed • Detailed design / engineering by licensed local engineer (owner's obligation) • Any owner-specific requirements not described above

## Simulated Yield
Simulated annual energy output — AE Solar Meteor 630W TopCon bifacial, Cyprus, fixed tilt 25° south
Parameter | Value | Unit | Notes
DC nameplate | 3.2004 | MWp | 5080 × 630 W
AC capacity | 2.760 | MWac | 24 × SUN2000-115KTL-M2 on-grid M2 string
DC/AC ratio | 1.160 | — | Preliminary; refine with PVSyst + layout
Bifaciality (datasheet) | 80 ± 5 % | — | AE CMER-132BDS Ver26.1.1 — higher than generic 75% placeholder
Tilt / azimuth | 25° / south | ° | Cyprus optimum — consistent with internal model
Ground albedo — high case | 0.70 | — | White stone / limestone gravel / coated hardstand
Ground albedo — low case | 0.25 | — | Bare soil / sparse vegetation
Specific yield — high (white albedo) | 2,165 | kWh/kWp·yr | 2150 × 80/75 bifaciality adjustment; PVSyst to confirm
Specific yield — low (soil) | 2,030 | kWh/kWp·yr | Conservative soil-albedo fixed-tilt benchmark
Annual energy — high case | 6,933 | MWh/yr | 3.2004 MWp × 2,165 kWh/kWp
Annual energy — high case | 6.93 | GWh/yr
Annual energy — low case | 6,497 | MWh/yr | 3.2004 MWp × 2,030 kWh/kWp
Degradation Year 1→end | −0.5 % / yr (est.) | — | n-Type TOPCon; AE datasheet states 87.4% at 30 yr
Performance ratio (indicative) | ~82–84 % | — | Including clipping, soiling, temperature; site-specific
Note | — | — | Full PVSyst simulation required with final layout, GCR, horizon shading, and confirmed bifaciality × albedo. Values above are engineering ROM only.