## Estimate — Relyz PV + BESS
Lighthief Cyprus — Investment Estimate ¦ Solar PV ~3.2 MWp + BESS Installation
Client: Relyz-PV ¦ Date: April 2026 ¦ Revision: 2.0 ¦ All prices in EUR (excl. VAT)
Item | Scope | Qty | Unit (€) | Line total (€)
SECTION A — Solar PV, ~3.2 MWp (string inverters, mounting, BOS, MV substation, civils, commissioning)
1 | PV modules — AE Solar Meteor AE630CMER-132BDS 630W TopCon bifacial (GG), EXW Rotterdam | 5080 | 86.62 | 440055
2 | String inverters — Huawei SUN2000-115KTL-M2, 115 kWac, 10 MPPT (27 units → 3.105 MWac; DC/AC 1.03) | 27 | 4576.7 | 123570.9
2a | Plant controller — Huawei SmartLogger 3000A03EU | 1 | 1049.12 | 1049.12
3 | Ground-mount structure — Helios 1-pole 2×portrait complete system (2,540 tables) | 2540 | 50 | 127000
4 | DC cabling — PV field (~32 km, supply) | 32238 | 1.06 | 34252.88
5 | AC cabling — LV (~8 km, supply) | 8000 | 3.75 | 30000
6 | BOS — cable trays, connectors, clamps, conduits, enclosures | 1 | 31250 | 31250
7 | Main LV switchboard + SCADA interface | 1 | 56250 | 56250
8 | Earthing & lightning protection — PV array / inverter area | 1 | 18750 | 18750
9 | Fire detection & suppression system — PV site | 1 | 35000 | 35000
10 | CCTV & perimeter security system | 1 | 22500 | 22500
11 | Civil works — levelling, access roads, hardstands, drainage | 1 | 81250 | 81250
12 | Commissioning, EAC energisation & handover documentation | 1 | 50000 | 50000
13 | MV substation — LV/MV step-up transformer + MV switchgear + kiosk civil works (~11 kV) | 1 | 175000 | 175000
14 | MV cable — substation to point of interconnection (variable, 3.2 MWp) | 1 | 40000 | 40000
15 | DSO grid-connection contribution — EAC POI works [TBC — subject to capacity study] | 1 | 43750 | 43750
16 | EAC metering cubicle — meter box, CT/VT, official seal | 1 | 12500 | 12500
17 | Licensed electrical engineer — design, SLDs, EAC application, co-ordination | 1 | 25000 | 25000
18 | Construction insurance — CAR + Third Party Liability (project duration) | 1 | 18750 | 18750
19 | Perimeter fencing — chain-link 1.5 m final height (~700 m perimeter) | 700 | 17.86 | 12503.75
20 | Spare parts & consumables kit — fuses, MC4 connectors, string combiner spares | 1 | 6250 | 6250
| Section A sub-total |  |  | 1384681.65
SECTION B — BESS Installation scope, 1 MW / 4 MWh (client-supplied battery containers, PCS & MV skid hardware)
⚠ Battery hardware (containers, PCS, MV skid) is client-supplied / procured separately. This section covers civil foundation, logistics coordination, electrical interfaces, protection engineering, LPS/SPD/earthing and commissioning support only.
B1 | Civil works — reinforced concrete pads (2×20 ft containers + MV skid) | 1 | 65000 | 65000
B2 | Logistics — port handling, customs, heavy transport to site | 1 | 7112.5 | 7112.5
B3 | LV cabling & cable tray within BESS yard | 1 | 8125 | 8125
B4 | MV feeder cable + terminations (skid → point of interconnection) | 1 | 7125 | 7125
B5 | Protection engineering (relay settings, co-ordination study) | 1 | 6875 | 6875
B6 | Remote trip interface + UPS / auxiliary power supply | 1 | 6625 | 6625
B7 | Lightning protection (LPS), surge protection (SPD) & earthing system | 1 | 35000 | 35000
B8 | BESS commissioning support & acceptance testing (client equipment) | 1 | 22500 | 22500
| Section B sub-total |  |  | 158362.5
| TOTAL — Sections A + B (excl. VAT) |  |  | 1543044.15
Excluded from this estimate: • VAT (19% Cyprus) • DSO grid-connection contribution listed as indicative (line 15) — subject to EAC capacity study; can vary significantly • Plot levelling beyond stated civil allowance • Detailed design / engineering certification beyond line 17 scope • Any owner-specific requirements not described above • O&M contract (available separately)

## Simulated Yield
Simulated annual energy — AE Solar Meteor 630W TopCon bifacial, Cyprus, fixed tilt 25° south
Parameter | Value | Unit | Notes
DC nameplate | 3.2004 | MWp | 5080 × 630 W
AC capacity | 2.760 | MWac | 27 × SUN2000-115KTL-M2
DC/AC ratio | 1.16 | — | Preliminary; refine with PVSyst
Bifaciality (AE datasheet) | 80 ± 5 % | — | CMER-132BDS Ver26.1.1
Tilt / azimuth | 25° / south | ° | Cyprus optimum
Albedo — high case | 0.70 | — | White stone / prepared hardstand
Albedo — low case | 0.25 | — | Bare soil / vegetation
Specific yield — high | 2,165 | kWh/kWp·yr | Bifaciality 80% + white albedo; solarpark-epc.md §7
Specific yield — low | 2,030 | kWh/kWp·yr | Conservative soil-albedo benchmark
Annual energy — high | 6,929 | MWh/yr | 3.2004 MWp × 2165 kWh/kWp
Annual energy — high | 6.93 | GWh/yr
Annual energy — low | 6,497 | MWh/yr
Year-1 degradation | −0.5 % / yr (est.) | — | n-Type TOPCon; AE warranty: 87.4% at year 30
Performance ratio | ~82–84 % | — | Indicative; PVSyst required for final model