## Quote 3.2MWp + BESS EPC
A/A | Equipment | Description | Qty | Unit buy € | Price basis | Extended buy € | Margin on sell | Unit client € | Line client €
1 | PV modules | AE Solar Meteor AE630CMER-132BDS 630W TopCon bifacial GG, EXW Rotterdam. Nameplate 3.2004 MWp = 5080×630W. | 5080 | 69.3 | AE Solar — EXW €/module | 352044 | 0% (pass-through) | 69.3 | 352044
2 | String inverters (on-grid M2) | Huawei SUN2000-115KTL-M2, 115 kWac, 10 MPPT. Closest M2 to 150kW; 24 units → 2.76 MWac, DC/AC 1.160. Pallet (3p) €3661.36/unit. | 24 | 3661.36 | Trikkis 01-03-2026 — pallet (3p) | 87872.64 | +20% | 4393.632 | 105447.17
2 | Plant controller | Huawei SmartLogger 3000A03EU — wholesale vs list. | 1 | 839.3 | Trikkis A8 wholesale | 839.3 | +20% | 1007.16 | 1007.16
3 | Mounting (ground) | Helios 1 pole 2× portrait steel; 2540 tables (5080÷2). Wholesale €/table. | 2540 | 40 | Trikkis Helios — wholesale | 101600 | +20% | 48 | 121920
4 | DC cabling | PV DC (~33 km BOQ × module ratio). | 32238 | 0.85 | Typical €/m | 27402.3 | +20% | 1.02 | 32882.76
5 | AC cabling | AC LV ~8 km BOQ. | 8000 | 3 | Typical €/m | 24000 | +20% | 3.6 | 28800
6 | BOS / trays / aux | Lump placeholder. | 1 | 25000 | Typical placeholder | 25000 | +20% | 30000 | 30000
7 | Main LV DB + SCADA tie-in | Lump placeholder. | 1 | 45000 | Typical placeholder | 45000 | +20% | 54000 | 54000
8 | Earthing & lightning (PV field) | Materials placeholder. | 1 | 15000 | Typical placeholder | 15000 | +20% | 18000 | 18000
9 | Fire fighting (PV site) | ~3 MWp class. | 1 | 28000 | Typical benchmark | 28000 | +20% | 33600 | 33600
10 | CCTV & perimeter security | Typical. | 1 | 18000 | Typical benchmark | 18000 | +20% | 21600 | 21600
11 | PV land civils | Typical. | 1 | 65000 | Typical benchmark | 65000 | +20% | 78000 | 78000
12 | PV commissioning & EAC | Typical. | 1 | 40000 | Typical benchmark | 40000 | +20% | 48000 | 48000
SECTION B — BESS EPC only (1 MW / 4 MWh, 2×20ft + MV skid)
B1 | BESS — concrete platforms & pads | 2×20ft + MV skid pads. | 1 | 52000 | Internal benchmark | 52000 | +20% | 62400 | 62400
B2 | BESS — port, customs, heavy haul | 2×20ft. | 1 | 5690 | Training guide scaled | 5690 | +20% | 6828 | 6828
B3 | BESS — LV cabling & aux tray |  | 1 | 6500 | Adder scaled | 6500 | +20% | 7800 | 7800
B4 | BESS — MV cabling + terminations |  | 1 | 5700 | Template adders | 5700 | +20% | 6840 | 6840
B5 | BESS — protection engineering |  | 1 | 5500 | Typical | 5500 | +20% | 6600 | 6600
B6 | BESS — remote trip + UPS/aux |  | 1 | 5300 | Template | 5300 | +20% | 6360 | 6360
B7 | BESS — LPS, SPD, earthing |  | 1 | 28000 | Subcontract lump | 28000 | +20% | 33600 | 33600
B8 | BESS — EPC commissioning support |  | 1 | 18000 | Typical | 18000 | +20% | 21600 | 21600
TOTALS

## Yield simulation
Parameter | Value | Unit | Notes
Module model | AE Solar Meteor AE630CMER-132BDS |  | Quoted EXW Rotterdam
Module power (STC) | 630 | Wp
Module count | 5080 | pcs | Target ~3.2 MWp nameplate
DC nameplate | 3.2004 | MWp | 5080×630W
Inverter | SUN2000-115KTL-M2 |  | 24×115kWac on-grid M2
AC capacity | 2.76 | MWac
DC/AC ratio | 1.16 | - | Preliminary; refine with PVSyst
Mount | Fixed tilt 25° south |  | Cyprus; bifacial rear sees sky + ground
Albedo (high case) | 0.7 | - | White stone / prepared pad
Albedo (low case) | 0.25 | - | Soil / sparse vegetation
Bifaciality (assumed) | 0.75 | - | TopCon class; confirm on AE datasheet
Specific yield (high) | 2150 | kWh/kWp/yr | solarpark-epc.md §7.1
Specific yield (low) | 2030 | kWh/kWp/yr | Soil albedo row
Annual energy (high) | 6881 | MWh/yr | Pdc_MWp × kWh/kWp
Annual energy (low) | 6497 | MWh/yr
Annual energy (high) | 6.881 | GWh/yr
Datasheet | AE_CMER_132_BDS_610_W_630_W Ver26.1.1 |  | docs/quotations/AEsolar/...
Bifaciality (datasheet) | 80 ± 5 % |  | Higher than 75% Agios placeholder — yield uplift ~few % vs internal model
630W STC (extracted) | Vmpp 42.0 V, Impp 15.00 A |  | 42×15=630 W; Voc/Isc columns in PDF text order ambiguous — verify on PDF table
630W bifacial equiv (datasheet) | 641 W @ 5% gain; 671 W @ 10% gain |  | Backside power gain scenarios vs front STC
Max system voltage / fuse | 1500 V; 30 A (per PDF extract) |  | Confirm in PDF electrical table
Specific yield (revised ballpark) | ~2165 | kWh/kWp/yr | Scaled from 2150: bifaciality 80/75 on bifacial increment only; PVSyst required
Annual energy (revised ballpark) | 6929 | MWh/yr | 3.2004 MWp × 2165 kWh/kWp

## Assumptions
3.2 MWp target: 5080×630 W = 3.2004 MWp. Inverters: 24×SUN2000-115KTL-M2 = 2.76 MWac, DC/AC ≈ 1.16.
Closest M2 to former 150kW MGO: 115KTL-M2 (then 100KTL-M2). MGO line is different series (7 MPPT).
Alt DC/AC: 25×115k→1.11; 28×100k→1.14; 23×115k→1.21; 32×100k→1.00 (clip).
AE datasheet CMER-132BDS Ver26.1.1: bifaciality 80±5%; 2383×1133×30 mm; 720 pcs/40HQ; 630W bifacial equiv 641W (5%) / 671W (10%) rear gain scenarios.