L	LIGHTHIEF

Energy Storage Solutions | Cyprus

Ref: LCY-RFI-VOLTUS-2026-003

Version: 1.0

Date: 20 February 2026

Priority: HIGH

REQUEST FOR INFORMATION

BMS Monitoring Depth, EMS Optimization & Market Capabilities, Cybersecurity Compliance

Cyprus BESS Portfolio — Client Technical Due Diligence Response

- PURPOSE

Dear Voltus Team,

We have received a detailed technical due diligence questionnaire from one of our investor-clients covering BMS monitoring depth, EMS optimization and market capabilities, cybersecurity compliance, and KPI tracking. Many items are covered by our existing documentation and the Linyang OEM specifications. However, several questions specifically relate to Voltus EMS software capabilities that we need to confirm before responding to the client.

VOLTUS INPUT REQUIRED

We have categorised each item below. Where we can answer from existing documentation, we have provided our

Response requested by: 25 February 2026

Client demo is scheduled for Wednesday 26 February. We need your input by Tuesday EOD at the latest to prepare the complete response package. Login credentials will be provided Monday.

Context: This questionnaire comes from a sophisticated investor who is evaluating our BESS package against bankability standards. The quality and detail of our response will directly impact contract progression. Please provide technically precise answers.

draft response. Where Voltus input is required, the your team.

tag is shown with a response field for

- BATTERY MONITORING SYSTEM — CELL-LEVEL MONITORING DEPTH

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 2.1 | Cell voltage monitoring | CONFIRMED | Linyang BMS (BMU Level 1): 52 voltage samples per BMU (2 BMUs per pack, 96 BMUs per container). Cell voltage range 0–5V, accuracy ±5 mV, sampling period ≤100 ms. Operational cell voltage range: 2.5V–3.65V. Warning thresholds at <2.6V / >3.55V, critical at <2.55V / >3.60V. Total per container: 4,992 cell voltage measurement points, continuously sampled at 10 Hz. |
| 2.2 | Cell temperature monitoring | CONFIRMED | Linyang BMS (BMU Level 1): 12 temperature samples per BMU, accuracy ±1°C, sampling period ≤200 ms. Range: -40°C to +105°C. Operational limits: charge 0°C to +55°C, discharge -20°C to +55°C. Warning at >50°C, critical at >53°C. Total per container: 1,152 temperature measurement points, sampled at 5 Hz. |
| 2.3 | Internal resistance tracking | VOLTUS INPUT REQUIRED | Linyang BMS monitors insulation resistance at system level. Question for Voltus: Does the Voltus EMS provide cell-level or module-level internal resistance tracking (AC impedance or DC resistance) as a derived metric from BMS data? If so, at what resolution and frequency? Is this logged historically for degradation trending? Voltus response: Yes — Voltus EMS can monitor and analyze internal resistance at the cell or module level, provided that the BMS supplies the relevant measurement data or intermediate parameters enabling its calculation. The functional scope depends on the capabilities of the specific BMS and includes: 1. Determination method - If the BMS provides direct DC resistance or AC impedance values, the EMS records and analyzes these parameters. 2. Resolution - cell level — if available in the BMS, - module level — if available in the BMS, - string / rack level — if available in the BMS. 3. Sampling frequency - aligned with the data update rate provided by the BMS, - typically from 1 s to 60 s for operational data, - diagnostic values (e.g. resistance test results) according to the BMS schedule or event-based. - To limit the amount of data stored in the database, we propose aggregating this parameter and storing minimum, maximum, and average values at 5-minute intervals. 4. Historical logging and degradation analysis Yes — all available or derived values are historically stored in the EMS database and can be used for: - cell and module degradation trending, - anomaly detection and early warning, - comparison between modules / strings, - predictive battery health diagnostics (SOH), - service reporting and long-term analysis. 5. Additional (optional) - automatic detection of resistance increase above defined thresholds, - diagnostic alarms, - correlation with temperature, SOC, and operating cycles. |
| 2.4 | Cell imbalance detection | CONFIRMED | Linyang BMS: Passive cell equalization with ≥80 mA balancing current. Imbalance warning threshold: >30 mV between cells; critical alarm: >50 mV. BMU-level monitoring ensures per-cell visibility. Equalization status and delta voltage are reported to BAMS (Level 3) and available via Modbus TCP to EMS. |
| 2.5 | SOC estimation accuracy <1% | VOLTUS INPUT REQUIRED | Linyang BMS (BCMU Level 2): SOC calculation accuracy is specified as ≤5%. Energy calculation error: ≤±2%. The client requests <1% SOC accuracy. This is significantly tighter than the BMS hardware specification. Question for Voltus: Does the Voltus EMS apply any enhanced SOC estimation algorithms (e.g., Kalman filtering, coulomb counting with drift correction, OCV correlation) on top of the BMS-reported SOC to achieve higher accuracy? What SOC accuracy can realistically be guaranteed at the EMS level? Can you provide a technical brief on the SOC estimation methodology? Voltus response: Currently, Voltus EMS relies on the SOC value reported by the BMS. In practice, the key factor determining SOC accuracy is the precision of current measurement over time (Ah integration), as this has the greatest impact on calculation accuracy. In addition, correction characteristics based on cell voltage are typically applied — particularly using the highest and lowest cell voltage — to periodically adjust SOC estimation. Achieving very high SOC accuracy at the supervisory (EMS) level is a complex task and strongly depends on measurement quality and battery modeling. If there is a formal requirement to achieve a specific accuracy (e.g. <1%), we can analyze this in detail and evaluate the feasibility of implementing enhanced estimation methods. However, from the perspective of system control and operational safety, SOC is not a critical parameter for EMS control algorithms. Our energy storage management strategy is primarily based on direct monitoring of electrochemical cell parameters, in particular: - maximum cell voltage, - minimum cell voltage, - voltage spread between cells. Based on these values, the EMS dynamically controls charge and discharge power limits to ensure that each cell operates within its optimal and safe operating range. Additionally, when cell voltage approaches defined operational limits, the EMS applies corrective SOC adjustments (upward or downward) to reflect the actual usable energy boundaries. This ensures that the reported SOC reaches the practical minimum or maximum level in line with real cell conditions. We do not rely solely on SOC — for energy storage management, the most important parameter is the actual cell voltage, which directly reflects the real operating condition of the battery and forms the foundation of the control strategy. |

| 2.6 | SOH estimation with degradation model | PARTIAL — VOLTUS INPUT REQUIRED | Confirmed from Linyang warranty: Degradation curves documented with guaranteed SOH milestones: Initial SOH: 98.5% at COD Year 5: ≥85% Year 10: ≥79.58% Year 15: ≥70% Cycle life: 7,000 cycles (25°C, 90% DoD, 0.5C/0.5C) to 70% EOL. Question for Voltus: Does the EMS include a real-time SOH estimation model that tracks actual degradation vs. the OEM warranty curve? Is this a physics-based model (impedance growth + capacity fade) or empirical? Is the degradation model configurable per cell chemistry (LFP-specific)? Voltus response : Currently, Voltus EMS does not calculate an additional independent SOH indicator. We rely on the SOH values provided by the BMS and store them historically for trending, reporting, and operational analysis. If such functionality is required, we can develop an EMS-level SOH estimation layer to track actual system degradation against the OEM warranty curve. The implementation would depend on the scope of data available from the BMS (e.g., capacity metrics, energy throughput, cycle count, temperature history, internal resistance or impedance diagnostics) and could be configured for the specific cell chemistry, including LFP. However, the most reliable method of determining the actual battery SOH remains a controlled capacity test based on a full charge–discharge cycle and direct measurement of the energy delivered to and withdrawn from the energy storage system. This approach provides a physically measurable value of usable capacity and is widely recognized as the most accurate practical method of verifying degradation. Voltus EMS can support this process through a dedicated capacity test function. The system can perform a controlled charge and discharge cycle under defined operating conditions, calculate the effective usable battery energy, and compare the result with nominal capacity and warranty reference values to determine the actual SOH. Capacity tests can be performed periodically — for example, once per year — or on demand as part of maintenance, warranty verification, or performance diagnostics. |
| --- | --- | --- | --- |

- ADVANCED DEGRADATION ANALYTICS

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 3.1 | Cycle counting algorithm | VOLTUS INPUT REQUIRED | Linyang warranty references cycle life (7,000 equivalent full cycles). BMS tracks cumulative charge/discharge energy. Question for Voltus: Does the EMS implement a rainflow cycle counting algorithm (or equivalent) to accurately count partial cycles and map them to equivalent full cycles? Is this per-container or per- cluster? Is the methodology aligned with IEC 62660-1? Voltus response: Currently, Voltus EMS does not implement a rainflow algorithm for cycle counting as a standard feature. In the typical configuration, we rely on data provided by the BMS, particularly cumulative charge and discharge energy throughput, which can be used to calculate equivalent full cycles (EFC). The EMS reads and records parameters such as SOC, SOH, and charge/discharge energy at the level of each container and each rack. This allows independent calculation of cycling usage (EFC) separately for containers and individual racks, enabling more precise monitoring of operation and detection of uneven utilization within the system. If a more advanced method of counting partial cycles is required (e.g., rainflow or equivalent load cycle analysis), such functionality can be implemented at the EMS level. |
| 3.2 | Throughput-based degradation tracking | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS track cumulative energy throughput (MWh in + MWh out) per container/cluster and correlate it with capacity degradation? Is this presented as a degradation-per- MWh metric? Can it differentiate between charge and discharge throughput impact? Voltus response: Yes — Voltus EMS monitors cumulative energy throughput (MWh charged and MWh discharged) at the container and cluster level, and depending on data availability, also at the rack level. These data are historically recorded and used for operational analysis of the system as well as comparisons between individual units. Based on this, it is possible to perform correlation analysis between energy throughput and observed degradation (e.g., changes in SOH reported by the BMS or results from capacity tests). The EMS typically presents usage and degradation trends over time, cycle count, and energy throughput. If required, degradation can be reported as a “degradation per MWh throughput” metric. This can be configured within the EMS — for example, as a reduction in SOH or effective capacity relative to the cumulative energy processed by the system. The EMS tracks charge and discharge energy as separate measured quantities, enabling independent analysis of their respective impact on degradation. This allows evaluation of load asymmetry or the influence of specific operating strategies (charging vs. discharging profiles) on battery aging. In addition, the EMS includes a built-in power balancing function across containers designed to equalize SOC levels among all units. This ensures that the entire energy storage system is utilized evenly, reducing uneven wear between containers and supporting more uniform degradation across the installation. The scope and level of detail of such analysis depend on the quality and resolution of the data available from the BMS and the EMS reporting configuration |
| 3.3 | Calendar aging model | VOLTUS INPUT REQUIRED | Our Linyang degradation data shows first-year SOH drop of ~4–5% across all usage profiles, suggesting calendar aging is a meaningful contributor alongside cycling. Question for Voltus: Does the EMS include a calendar aging model that accounts for time-at-temperature and SOC-at-rest effects? Is this separable from cycle aging in the degradation dashboard? What inputs does it use (ambient temperature, average SOC, time)? Voltus response: Currently, Voltus EMS does not include a dedicated independent computational model for calendar aging by default. We typically rely on SOH values reported by the BMS and on operational trend analysis (operating time, energy throughput, cycles). |
| 3.4 | Dynamic DoD impact modelling | VOLTUS INPUT REQUIRED | Linyang specifications include cycle life at both 100% DoD (6,000 cycles to 80% SOH) and 90% DoD (7,000–8,000 cycles to 70% SOH), confirming DoD-dependent degradation. Question for Voltus: Does the EMS dynamically model the impact of varying DoD on battery degradation? Can it adjust dispatch strategies to optimize between revenue and battery lifetime? Is the DoD-cycle life curve configurable? Voltus response: Voltus EMS does not rely on a dynamic degradation model based directly on varying DoD. Instead, Voltus has developed its own control methodology that adjusts power limiting strategies based on real-time cell voltage and temperature conditions, ensuring operation within electrochemically safe and optimal ranges that do not accelerate degradation. This control approach is the result of over three years of research, field experience, and implementation across multiple energy storage projects. Based on operational experience, Voltus does not restrict battery operation in the EMS as long as the system is operating within safe and optimal electrochemical limits. From an investor’s perspective, limiting battery operation while it remains within its intended operating range is generally not acceptable, as the system is expected to deliver its contracted performance. However, if required by the investor or project owner, Voltus can adjust operational thresholds — shifting them from standard safety boundaries toward more conservative optimal lifetime-oriented limits. This can further reduce long-term degradation but will also result in more restrictive operation and reduced usable energy or power availability of the storage system. |
| 3.5 | Predictive EOL forecasting | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS provide a predictive End-of-Life forecast based on actual usage data (cycles, throughput, temperature history, calendar time)? Can it project the date at which SOH will reach the warranty threshold (70%)? Is this updated dynamically as operating conditions change? Currently, Voltus EMS does not include a built-in predictive EOL model as a standard feature that determines a specific date at which a defined SOH threshold (e.g. 70%) will be reached based on a comprehensive degradation model. By default, the system: - monitors and archives SOH reported by the BMS, - records operational history (cycles, energy throughput, temperature, operating time), - enables analysis of degradation trends over time. Based on this, it is possible to observe the rate of SOH decline and compare it with reference or warranty curves. In addition, within the SCADA system, Voltus provides a general signal prediction function. This functionality allows selected parameters to be forecast based on historical data trends and configured prediction models. Using this capability, parameters such as SOH or other degradation-related indicators can be projected forward in time to estimate future values under assumed operating conditions. The prediction is continuously updated as new operational data becomes available. If formal EOL forecasting is required, Voltus can implement a dedicated predictive model that: - estimates future degradation based on actual operational data (cycles, energy, temperature, time), - forecasts when a defined SOH threshold (e.g. 70%) will be reached, - updates the forecast dynamically as operating conditions change, - enables scenario-based analysis of how operating strategies affect battery lifetime. |

Voltus response:

Currently, Voltus EMS does not include a built-in predictive EOL model as a standard feature that would determine a specific date at which a defined SOH threshold (e.g. 70%) will be reached based on a comprehensive analysis of operational data.

By default, the system:

- monitors and archives SOH reported by the BMS,

- records operational history (cycles, energy throughput, temperature, operating time),

- enables analysis of degradation trends over time.

Based on this, it is possible to observe the rate of SOH decline and compare it with reference or warranty curves.

If formal EOL forecasting is required, Voltus can implement a predictive model that:

- estimates future degradation based on actual operational data (cycles, energy, temperature, time),

- forecasts when a defined SOH threshold (e.g. 70%) will be reached,

- updates the forecast dynamically as operating conditions change,

- enables scenario-based analysis of how operating strategies affect battery lifetime.

- THERMAL & SAFETY MONITORING

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 4.1 | Thermal runaway early detection | CONFIRMED | Multi-layer detection system per container: Cell-level: 1,152 temperature sensors (BMU), ≤200 ms sampling, warning >50°C, critical >53°C Gas detection: 2× H₂ combustible gas detectors + 2× CO sensors per container Smoke detection: 2× photoelectric smoke detectors per container Heat detection: 2× spot-type heat detectors per container Pack-level: 48× CO + temperature detection nozzles integrated per pack Chemistry advantage: LFP (Lithium Iron Phosphate) is inherently the most thermally stable Li-ion chemistry. UL 9540A testing PASSED with no thermal propagation between modules. |
| 4.2 | Gas detection integration | CONFIRMED | Integrated into fire control panel per container: 2× H₂ (combustible gas) detectors — triggers explosion-proof fans at low threshold, emergency ventilation at high threshold 2× CO (carbon monoxide) sensors — early indicator of cell decomposition Explosion vent panel for pressure relief Explosion-proof exhaust fan for gas evacuation Gas thresholds are tied to the 4-stage alarm escalation sequence with automatic suppression activation. |
| 4.3 | Hotspot localization | PARTIAL — VOLTUS INPUT REQUIRED | BMS capability: 12 temperature sensors per BMU (96 BMUs per container = 1,152 points) provides module-level spatial resolution for temperature mapping. Min/Max cell temperature per cluster reported to BAMS and forwarded to EMS. Question for Voltus: Does the Voltus EMS provide a thermal map or hotspot visualization feature that leverages the 1,152 temperature data points per container? Can it identify and alert on localized thermal anomalies (e.g., specific rack/pack running consistently hotter)? Voltus response: Yes — Voltus EMS can utilize high-resolution temperature data provided by the BMS for detailed visualization and analysis of temperature distribution within the energy storage system. The system enables temperature monitoring at the container, rack, or module level (depending on the availability and structure of BMS data), including visualization of temperature distribution and identification of areas with elevated temperatures (hotspots). The EMS can detect localized thermal anomalies such as: - a rack or module consistently operating at a higher temperature than others, - excessive temperature differences between units, - upward temperature trends in a specific location, - exceedance of defined alarm thresholds. The system can generate alarms and diagnostic events when thermal irregularities are detected, and it supports historical analysis and temperature distribution trend monitoring over time. The level of visualization detail (e.g., 2D/3D thermal mapping or tabular presentation) depends on the SCADA/EMS configuration and the structure of data provided by the BMS. |
| 4.4 | HVAC performance monitoring | PARTIAL — VOLTUS INPUT REQUIRED | System specification: Liquid cooling (ethylene glycol + water), 45 kW capacity (0.5C) / 60 kW (1C). Internal target: 25±5°C. BMS controls thermal management start-stop and monitors temperature deviation. Question for Voltus: Does the EMS monitor HVAC/cooling system performance metrics (COP, coolant flow rate, inlet/outlet delta-T, compressor run-time, energy consumption)? Are HVAC efficiency degradation trends tracked? Are alerts generated for cooling performance degradation? |

|  |  |  | Voltus response: Yes — Voltus EMS can monitor HVAC/cooling system performance parameters, provided they are available through the communication interface of the cooling system (e.g., BMS, chiller controller, or building management system). Monitored parameters (depending on available data) - cooling system energy consumption, - compressor and auxiliary equipment run-time, - coolant temperatures (inlet / outlet), - temperature differential (delta-T), - coolant flow rate, - cooling system operating status and modes. Based on these data, the EMS can also calculate performance indicators (e.g., energy efficiency metrics or COP), provided the required measurements are available. Efficiency trend tracking The EMS supports historical analysis and trend monitoring of cooling system operating parameters, enabling identification of gradual performance degradation, such as: - reduced cooling effectiveness under similar load conditions, - increased compressor run-time, - changes in delta-T characteristics, - rising energy consumption per unit of cooling capacity. Alarms and diagnostics The system can generate alarms and diagnostic events in case of: - temperature threshold exceedance, - abnormal cooling system operating parameters, - performance degradation relative to defined reference values, - detected trends indicating declining system efficiency. The scope of monitoring and diagnostics depends on signal availability and the communication integration of the cooling system with the EMS. |
| --- | --- | --- | --- |
| 4.5 | Fire system status integration | CONFIRMED | Fully integrated fire detection and suppression system per container: Fire control panel with multi-zone detection 4-stage alarm escalation: Primary (single detector) → Secondary (smoke+heat) → Gas threshold → Pack-level alarm Automatic aerosol suppression (6× container-level + 96× pack- level units) 30-second countdown before suppression discharge Audible/visual alarms (indoor + outdoor) BMS automatic shutdown on fire alarm Water firefighting system as backup Fire system status signals are available to the EMS via BMS/BAMS Modbus interface. |

- FAULT DETECTION & DIAGNOSTICS

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 5.1 | Real-time fault classification | PARTIAL — VOLTUS INPUT REQUIRED | Linyang BMS fault categories: Overvoltage, undervoltage, overcurrent, short circuit, over/under temperature, insulation fault, leakage, cell imbalance. Each has warning and critical severity levels. Question for Voltus: Does the Voltus EMS provide fault classification beyond the BMS-level alarms? Specifically: (a) automatic categorization of faults by type/severity/location, (b) correlation of multiple alarm signals to identify root fault vs. cascading effects, (c) fault history analytics with classification trends? Voltus response: Yes — Voltus EMS can provide extended event classification and analysis beyond the basic alarms reported by the BMS, depending on system configuration and the scope of available data. (a) Automatic event classification The EMS can automatically classify events by: - fault type (e.g., electrical, thermal, communication, operational), - severity level (information, warning, alarm, critical), - location (container, rack, module, component), - source system (BMS, PCS, HVAC, auxiliary systems). In addition, the system allows user-defined configuration and customization of event categories, alarm thresholds, and classification rules according to project or operational requirements. (b) Alarm correlation and root cause identification The system can analyze temporal and logical relationships between multiple alarm signals in order to: - identify primary fault events and secondary cascade effects, - detect patterns of events leading to specific fault conditions, - filter secondary alarms to improve diagnostic clarity, - support root cause analysis. (c) Event history analytics The EMS maintains historical event records and supports analytical functions, including: - trending of specific fault occurrence frequency, - repeat-event analysis over time, - identification of areas or components with elevated fault rates, - statistical reporting of events and alarms. (d) Alarm notification and handling The system allows configuration of alarm notification methods, including: - voice notifications, - e-mail, - SMS. The EMS also supports multiple alarm acknowledgment methods, such as: - acknowledgment directly within the SCADA system, - voice communication and voice acknowledgment (if configured), - other configurable operator response procedures. The scope and level of analytical and notification functionality depend on system configuration and project requirements. |
| 5.2 | Predictive maintenance analytics | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS include predictive maintenance features? Specifically: (a) anomaly detection using statistical/ML models on sensor data trends, (b) remaining useful life estimation for key components (cells, contactors, cooling system), (c) automated maintenance scheduling based on condition monitoring? If available, what data history is required before predictive models become effective? Voltus response: Voltus EMS provides advanced system condition monitoring and operational trend analysis, which form the foundation for implementing predictive maintenance functionality. The scope of these features depends on system configuration and data availability. (a) Anomaly detection The EMS detects deviations from normal operating conditions based on signal trend analysis (e.g. temperature, voltage, current, HVAC parameters). More advanced statistical or machine learning models can be implemented as an extension of the system. (b) RUL (Remaining Useful Life) estimation The system continuously monitors component wear parameters and operational history. Based on this, RUL estimation models can be implemented for selected components (e.g. cells, contactors, cooling system), provided that appropriate diagnostic data is available. (c) Condition-based maintenance The EMS supports condition-based maintenance through parameter trend monitoring, diagnostic alarms, and generation of maintenance recommendations. Automatic service scheduling can be implemented as a configurable feature. In addition, the SCADA system includes a built-in scripting function that enables the creation of advanced diagnostic functions based on both real-time and historical data. This allows implementation of custom analytical algorithms and predictive logic tailored to the specific installation. |
| 5.3 | Root cause analysis engine | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS provide automated or assisted root cause analysis (RCA) for fault events? Can it correlate time- stamped data across BMS, PCS, thermal, and grid signals to help operators identify the origin of a fault chain? Is this manual (data replay) or automated (rule-based/ML)? Voltus response: Yes — Voltus EMS can provid functions that support root cause analysis (RCA) based on time-correlated data from multiple systems. Multi-system data correlation The EMS records and synchronizes time-stamped data from multiple sources, including: - BMS, - PCS / inverters, - cooling / HVAC systems, - grid measurements and supervisory systems. This enables reconstruction of event sequences and analysis of relationships between signals in order to identify the origin of a fault and its secondary effects. Analysis modes The system supports both: - manual analysis — through historical data replay, time-synchronized trend visualization, and event sequence analysis, - rule-assisted analysis — configurable correlation rules and diagnostic logic that identify typical cause-and-effect relationships. |
| 5.4 | Alarm prioritization logic | PARTIAL — VOLTUS INPUT REQUIRED | Confirmed system-level priority: Protection (local firmware, non- overridable) > DSO SCADA curtailment > DSO CB control > Market dispatch. BMS alarms have warning vs. critical severity. Question for Voltus: Does the EMS provide configurable alarm prioritization within the SCADA/dashboard? (a) Severity-based filtering (info/warning/critical/emergency), (b) alarm suppression for known conditions, (c) alarm shelving during maintenance, (d) escalation rules (e.g., unacknowledged critical alarm → SMS/email after X minutes)? Voltus response: Yes — Voltus EMS provides fully configurable alarm prioritization and alarm management within the SCADA system. (a) Severity-based filtering Alarms can be classified and filtered by severity level (e.g. information, warning, alarm, critical, emergency). Operators can view and handle events according to the defined priority hierarchy. (b) Escalation rules The EMS supports configurable escalation rules, such as: - SMS / e-mail / voice notifications, - escalation if an alarm remains unacknowledged for a defined time, - multi-level notification scenarios for different operational roles. The system allows alarm management policies to be tailored to operator, investor, and site operational procedures. |

- DATA INFRASTRUCTURE

#

6.1

Client Requirement

High-resolution data logging (1s or sub- second)

Status

CONFIRMED

Response / Voltus Input

BMS hardware: Voltage sampling ≤100 ms (10 Hz), temperature

≤200 ms (5 Hz), current ≤100 ms

EMS data logging: 1-second resolution for real-time measurements, 7-day retention for raw data

Performance data: 1-minute resolution, 1-year full retention, 10- year aggregated

6.2

Event-triggered recording

VOLTUS INPUT

REQUIRED

Event logs are captured immediately with 5-year retention. Curtailment events are logged with start/end timestamps, commanded vs. achieved values, and curtailed energy (kWh).

Question for Voltus: Does the EMS support event-triggered high- resolution recording (e.g., increase logging frequency from 1s to sub-second when a fault/transient is detected)? Similar to a disturbance recorder or oscillography function? What triggers are configurable?

Voltus response:

Yes — Voltus EMS can perform event-triggered high-resolution data recording, provided that the available measurement infrastructure and data source sampling rates support it.

Under normal operation, the system records data at the standard operational resolution. When a defined event is detected, selected signals can automatically switch to higher-frequency recording (sub-second resolution) within a defined time window.

Typical use cases

- dynamic disturbance analysis,

- diagnostics of fast transient events,

- detailed fault sequence analysis,

- verification of control system response.

Configurable triggers (examples)

- BMS or PCS alarms (e.g. overvoltage, trip, fault),

- threshold exceedance for voltage, current, or temperature,

- rapid changes in power or frequency,

- grid events or DSO commands,

- protection system activation,

- user-defined system events,

- logical rules or SCADA scripts.

The set of signals recorded at high resolution, the sampling frequency, and the duration of pre-event and post-event recording are configurable.

This functionality depends on the available resolution of source data (BMS, PCS, meters, measurement systems) and the configuration of the EMS/SCADA recording system.

6.3

Time synchronization via NTP/GPS

PARTIAL — VOLTUS

INPUT

REQUIRED

GPS antenna is listed as required hardware per park (Lighthief to procure). IEC 60870-5-104 protocol requires time synchronization for DSO communication.

Question for Voltus: Does the WAGO PFC200 / Voltus EMS support NTP and/or GPS-based time synchronization? What is the time accuracy achieved? Is the time source configurable (NTP primary, GPS fallback, or vice versa)? Is time sync status monitored and alarmed?

Voltus response:

Yes — the WAGO PFC200 controller and Voltus EMS support time synchronization via both NTP, depending on system configuration and available infrastructure.

Supported time sources

- NTP servers (local or external),

- GPS via an NTP time server,

- configurable time source priority (e.g. NTP as primary and GPS as backup — or vice versa).

Synchronization accuracy

- NTP (typical industrial network): usually in the millisecond range (depending on network quality),

- GPS: typically sub-millisecond reference time accuracy (depending on the receiver / time server used).

6.4

6.5

API export capability

Data retention policy

CONFIRMED

CONFIRMED

REST API: Available for cloud integration and external system data exchange

Export formats: CSV (analysis/reporting), JSON (API integration), IEC 61968 CIM (utility data exchange), Excel (client reports)

| Data Type | Resolution | Retention |
| --- | --- | --- |
| Real-time measurements | 1 second | 7 days (raw) |
| Event logs | Immediate | 5 years |

Reporting: Monthly performance report (within 10 business days), quarterly health report (within 15 business days), annual review (within 30 days)

|  |  |  |  | Performance data | 1 minute | 1 year (full), 10 years (aggregated) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Alarm history | Immediate | 5 years |  |

- EMS — OPTIMIZATION CAPABILITY

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 7.1 | Multi-objective optimization engine | VOLTUS INPUT REQUIRED | Voltus EMS supports energy optimization including peak shaving, load shifting, and arbitrage. Multi-PCS coordination confirmed. Question for Voltus: Please describe the optimization engine architecture: (a) Is it a multi-objective optimizer (e.g., maximize revenue while minimizing degradation and maintaining grid obligations)? (b) What optimization algorithm is used (LP, MILP, dynamic programming, heuristic)? (c) What is the optimization horizon (rolling 24h, 48h, week-ahead)? (d) What is the dispatch resolution (1 min, 5 min, 15 min)? Voltus response: Yes — Voltus EMS applies a multi-objective approach; however, in practice the operation of the entire system managed by a single EMS is executed according to the selected operating mode and priorities defined based on project requirements. For example, commands from DSO and TSO operators always take priority over optimization objectives. In addition, grid constraints and operational limits imposed by service requirements or equipment manufacturers have the highest operational priority, as they ensure safe operation and protection of individual system components. (a) Optimization nature and system control logic The EMS distributes the requested power among available devices according to the selected control logic. The system provides several power distribution modes, including: - equal distribution of the setpoint across all available units, - distribution aimed at balancing SOC levels across energy storage units, - however, the distribution always accounts for available capacity and operational limits of individual units. If any device is unable to meet its assigned power level (e.g. due to temperature, voltage, or service-related constraints), the load is automatically redistributed to the remaining units, provided their operating conditions allow it. If the required system-level power cannot be achieved, the operator is informed that the setpoint cannot be fulfilled. Optimization procedures and protection mechanisms operate in parallel. The EMS continuously monitors operating parameters at the container, module, and individual cell levels. If operational limits are exceeded for a specific unit, its power is reduced, and the required power is transferred to other available parts of the system where possible. This approach ensures that: - higher-level system commands and grid requirements are always respected, - equipment safety and protection have absolute priority, - the system strives for balanced and optimal utilization of all units, - optimization objectives are achieved within permissible operating limits. (b) Optimization methods The optimizer architecture is modular and application-dependent. A combination of methods is used, including: - deterministic constrained optimization (e.g. LP / MILP) for scheduling, - heuristic and rule-based algorithms for real-time operational control, - adaptive control strategies responding to current system conditions. The specific method depends on project requirements, available data, and model complexity. (c) Optimization horizon The EMS supports rolling horizon optimization. Typical configurations include: - 12 hours, - 24 hours (most common), - 48 hours, - multi-day or week-ahead scenarios (e.g. strategic planning or simulation). The optimization horizon is fully configurable. (d) Dispatch resolution Dispatch resolution depends on the application and market or grid integration. Typical values include: - 15 minutes — energy market participation and scheduling, - 5 minutes — ancillary services and operational optimization, - 1 minute or faster — local power control and dynamic regulation. The EMS can operate simultaneously at multiple time resolutions — combining long-term planning with short-term real-time control. |
| 7.2 | Revenue stacking optimization | VOLTUS INPUT REQUIRED | Question for Voltus: Can the EMS simultaneously optimize across multiple revenue streams (e.g., energy arbitrage + FCR + aFRR + DSO curtailment avoidance)? How does it handle conflicting obligations between services? Can revenue stream priorities be configured? Voltus response: Yes — Voltus EMS can simultaneously manage and optimize system operation across multiple revenue streams, such as energy arbitrage, ancillary services (e.g. FCR, aFRR), grid obligations, and constraints resulting from operator commands. Multi-service operation The EMS considers all active operational commitments and available system resources (SOC, power capacity, device availability, technical constraints), and determines a feasible operating schedule that satisfies both contractual and technical requirements. Handling conflicts between services When conflicts arise between obligations (e.g. reserve capacity for regulation vs. energy arbitrage), the EMS applies a defined control priority hierarchy. In particular: - system operator commands (DSO / TSO) always take priority, - technical constraints and equipment protection are strictly enforced, - contracted ancillary service obligations are fulfilled according to their assigned priority, - economic optimization is performed within the remaining operational flexibility. Configurable revenue priorities Revenue stream priorities can be configured at the project or operational level. This includes, for example: - assigning economic weights to specific services, - defining minimum power or energy reserves for selected services, - specifying service activation hierarchy, - adjusting strategies based on market schedules or operator requirements. |
| 7.3 | Constraint-aware dispatch | PARTIAL — VOLTUS INPUT REQUIRED | Confirmed constraints: DSO curtailment commands have absolute priority over market dispatch. Protection (local firmware) cannot be overridden. BMS enforces voltage, current, and temperature limits. Question for Voltus: Beyond protection and DSO constraints, does the optimizer account for: (a) SOC limits (min/max), (b) ramp rate limits, (c) C-rate limits, (d) temperature-dependent power derating, (e) grid connection capacity limits, (f) contractual availability requirements? Voltus response: Yes — beyond protection-level constraints and DSO commands, the Voltus EMS optimization engine incorporates the full set of technical and contractual system constraints. In particular, the optimizer accounts for: (a) SOC limits (min / max) - configurable operational SOC boundaries, - energy reserves for ancillary services or contractual requirements, - limits related to battery lifetime protection. (b) Ramp rate limits - maximum charge and discharge power change rates, - constraints imposed by PCS, grid requirements, or operator specifications. (c) C-rate limits - current limits based on battery characteristics, - dependency on operating conditions (e.g. SOC, temperature, system state). (d) Temperature-dependent power derating - dynamic power limits based on cell, module, or cooling system temperature, - automatic adjustment of available operating power. (e) Grid connection capacity limits - import and export limits defined by the grid connection agreement, - constraints imposed by distribution or transmission operators, - local infrastructure limitations. (f) Contractual availability requirements - minimum power or energy availability for contracted services, - maintenance of operational reserves, - constraints resulting from market schedules or system agreements. All of the above are treated as hard optimization constraints, meaning that dispatch schedules and control decisions are always consistent with the actual technical capabilities of the system and contractual obligations. This ensures that economic optimization is performed strictly within safe and permissible operating limits. |
| 7.4 | Degradation-aware dispatch | VOLTUS INPUT REQUIRED | Degradation tracking and warranty monitoring are referenced as EMS features. Battery life monitoring is listed in BESS-specific features. Question for Voltus: Does the optimization engine incorporate a degradation cost function in its dispatch decisions? Specifically: (a) Does it assign a $/MWh degradation cost to each charge/discharge cycle? (b) Can it reduce cycling when marginal revenue is below marginal degradation cost? (c) Is the degradation model calibrated to Linyang LFP cycle life curves? (d) Can it adjust DoD dynamically based on price signals? Voltus response: Currently, Voltus EMS does not use a full battery lifetime optimization model based on detailed electrochemical degradation economics as a standard feature. However, the system does already account for economic profitability of charging and discharging under dynamic market prices, including system efficiency losses. In particular, the EMS evaluates whether price spreads are sufficient to justify cycling. If the difference between maximum and minimum prices within the optimization horizon is too small to compensate for round-trip efficiency losses, the energy storage system will wait and avoid arbitrage, rather than performing economically inefficient charge–discharge cycles. Battery lifetime protection is therefore implemented primarily through: - operational constraints and safe operating ranges, - real-time monitoring of cell voltage, temperature, and current limits, - efficiency-aware economic dispatch logic. (a) Degradation cost expressed in $/MWh or per cycle By default, the EMS does not assign an explicit financial degradation cost to each cycle or energy throughput. However, the optimization framework can be extended to include a degradation cost expressed in financial terms ($/MWh or per cycle) as part of the objective function. This allows dispatch decisions to account not only for market price spreads and efficiency losses, but also for the economic value of battery wear. (b) Cycle avoidance when marginal revenue is below degradation cost In the standard configuration, cycling is avoided when price spreads are insufficient to cover efficiency losses. If a financial degradation model is implemented, the EMS can further limit cycling when marginal revenue is lower than the combined cost of efficiency losses and degradation. (c) Calibration to OEM degradation curves (e.g. Linyang LFP) If required, the degradation model can be calibrated using manufacturer data, including cycle-life curves for specific chemistries such as LFP. This is configurable and project-dependent rather than a default setting. (d) Dynamic DoD adjustment based on price signals Operational SOC / DoD limits are normally configured as system parameters. Advanced control strategies can be implemented to dynamically adjust the operating window in response to price signals — for example expanding DoD during high-value periods and narrowing it when economic incentives are lower. Summary Voltus EMS already incorporates economic efficiency considerations in arbitrage decisions and prevents cycling when market conditions are not favorable. Financial degradation cost modeling, dynamic DoD strategies, and full revenue-versus-lifetime optimization can be implemented as configurable extensions of the optimization engine when required by project economics, warranty strategy, or asset management objectives. |

| 7.5 | Stochastic optimization | VOLTUS INPUT REQUIRED | Question for Voltus: Does the optimizer use stochastic methods to account for uncertainty in price forecasts, RES generation, and load? (a) Is it scenario-based (Monte Carlo) or robust optimization? (b) How many scenarios are evaluated? (c) What is the computation time per optimization run? (d) Does it incorporate confidence intervals on forecasts? Voltus response: Response (Voltus) In the standard configuration, Voltus EMS optimizes system operation based on day-ahead energy prices and RES generation forecasts (e.g. derived from weather forecasts). This means the system uses a single baseline forecast rather than full probabilistic models. If required by the project, the EMS can be extended with more advanced approaches that account for forecast uncertainty. (a) Handling forecast uncertainty By default, the optimization does not use stochastic methods. Instead, the user configures operational logic parameters according to their needs, such as: - charging and discharging price thresholds, - number of charging and discharging hours, - charge and discharge power levels, - import and export power limits, - SOC range allocated for price arbitrage. Additional functionality can be implemented if required, such as: - analysis of different scenarios (e.g. low / medium / high price levels), - conservative operating strategies accounting for forecast uncertainty, - planning and simulation scenarios. (b) Number of scenarios There is no fixed number of scenarios. The user configures the control logic and can monitor calculated operating scenarios in real time. For each scenario, it is possible to define: - operational priorities, - time periods when a given strategy applies, - different system control parameters. (c) Computation time In standard operation, optimization runs quickly — typically within a few seconds — allowing rapid evaluation of different operating strategies. (d) Forecast confidence intervals By default, the system uses a baseline forecast. If forecast uncertainty ranges are available, they can be incorporated through scenarios or additional safety margins. Summary The EMS typically optimizes operation based on energy price data and RES generation forecasts (e.g. weather-based forecasts). If a more advanced approach that explicitly accounts for market or production uncertainty is required, it can be implemented as an additional SCADA functionality. Built-in scripting tools and dedicated widgets allow users to calculate and visualize different operating scenarios. |
| --- | --- | --- | --- |

- MARKET INTEGRATION CAPABILITY

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 8.1 | Day-ahead market interface | VOLTUS INPUT REQUIRED | Market participation status is tracked (Address 102: 0=Deactivated, 1=Activated). Aggregators (ABIO, Synenergia) handle market interface for grouped parks. Question for Voltus: Does the EMS provide a direct interface to day-ahead electricity markets? (a) What market platforms are supported? (b) Can it generate and submit day-ahead bid schedules automatically? (c) Is there a day-ahead optimization module that produces an optimal charge/discharge schedule based on price forecasts? (d) How does it interface with third-party aggregators (ABIO, Synenergia)? Voltus response: Voltus EMS can operate either with direct market participation or through external aggregators, depending on the project architecture and market participation model. (a) Supported market platforms The EMS is not limited to a single specific market platform. Integration depends on the communication interfaces available within the project. Possible integrations include: - API connections to market platforms, - data exchange with trading systems, - operation via aggregators or asset portfolio managers. The scope of integration is configurable and depends on local market requirements. (b) Automatic generation and submission of day-ahead bids The EMS can automatically generate operating schedules for the energy storage system based on price forecasts and technical constraints. Automatic submission of market bids depends on the integration model: - with direct integration to a trading platform or API — automatic submission is possible, - when working through an aggregator — the schedule is provided to the aggregator’s system, which performs the market submission. (c) Day-ahead optimization module Yes — the EMS includes a day-ahead planning function. Based on energy price forecasts and system availability, it generates an optimal charge and discharge schedule that accounts for: - technical system constraints, - available power and energy capacity, - operational commitments, - user-defined operating strategy. (d) Integration with aggregators (e.g. ABIO, Synenergia) The EMS interfaces with aggregators through operational and planning data exchange, including: - providing available power and system flexibility, - sending operating schedules, - receiving dispatch commands or service activation signals, - exchanging market and operational status information. Communication may be implemented via API, industrial communication protocols, or project-specific interfaces. Summary Voltus EMS supports day-ahead planning and schedule generation based on price forecasts. Market participation can be implemented either directly or through aggregators, with communication methods configurable to match the project’s market participation structure. |
| 8.2 | Intraday continuous trading | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS support intraday continuous trading? (a) Can it revise dispatch schedules in near-real-time based on updated price signals? (b) What is the minimum lead time for schedule revision? (c) Can it interface with intraday trading platforms? (d) Is this relevant to the Cyprus market structure (currently under development by CERA/TSO)? Voltus response: Yes — Voltus EMS can support system operation under intraday trading conditions, depending on the availability of market signals and the method of integration with trading platforms or aggregators. (a) Near real-time schedule updates Yes. The EMS can adjust the energy storage operating schedule at short time intervals based on: - updated price signals, - changes in available power or energy, - operator or aggregator commands, - real-time system operating conditions. The system operates using rolling optimization, meaning the operating plan can be recalculated regularly. (b) Minimum lead time for schedule revision This depends on system configuration, market integration, and operator or trading platform requirements. Technically, the EMS can respond very quickly (seconds to minutes), but the actual minimum lead time is determined by market rules and operational requirements. (c) Integration with intraday trading platforms Yes — integration with intraday platforms is possible through: - trading system APIs, - aggregator interfaces, - exchange of planning and operational data. The scope of integration depends on market infrastructure and the participation model. (d) Relevance to the Cyprus market structure This functionality can be applied in market structures that support intraday trading or equivalent mechanisms. In the case of Cyprus, where the electricity market model is being developed by CERA / TSO, the EMS architecture is designed to adapt to future market mechanisms, including potential intraday trading once formally implemented. Summary Voltus EMS can update operating schedules at short intervals, integrate with intraday trading platforms (directly or via aggregators), and adapt to specific market structures — including evolving market frameworks such as those in Cyprus. |
| 8.3 | Ancillary services bidding | PARTIAL — VOLTUS INPUT REQUIRED | Confirmed grid services: FCR: Activation <30s (Voltus target <1s), full response <30s (target <10s), configurable droop (4–6%), deadband (±10 mHz) aFRR: Activation <5 min (Voltus target <30s), ramp rate 10– 100% PM/min, accuracy ±5% (target ±2%) Question for Voltus: Beyond the real-time response capability, does the EMS support the bidding process for ancillary services? (a) Can it calculate available capacity for bidding (accounting for SOC, degradation, other commitments)? (b) Can it generate ancillary service bid volumes automatically? (c) Is there an API or protocol for submitting bids to the TSO/market operator? Voltus response: Yes — in addition to real-time response capability (FCR, aFRR), Voltus EMS supports preparation of system resources for participation in ancillary services markets. The scope of functionality depends on the market participation model (direct or via aggregator) and integration with market systems. (a) Calculation of available capacity for bidding Yes. The EMS calculates the available regulation capacity that can be offered, taking into account: - current and forecast SOC, - available energy window for upward and downward regulation, - other active system commitments, - technical and operational constraints, - equipment availability and required safety reserves. Based on this, the system determines safe and realistically available regulation capacity. (b) Generation of bid volumes The EMS does not normally create formal market bids, as the bidding process is handled by a trading system or aggregator. However, the EMS provides all data required to prepare bids, including: - time-based available capacity profiles, - forecast resource availability, - operational constraints, - recommended operating ranges. These data can be automatically transmitted to an aggregator or trading platform. (c) Submission of bids to the market operator / TSO Voltus EMS is not a market bidding platform. Formal market submissions are performed by an aggregator or trading system. The EMS provides operational data used in the bidding process, such as: - available regulation capacity, - availability profiles, - system status and constraints, - confirmation of service delivery capability. Communication can be implemented via API, industrial protocols, or project-specific interfaces. The EMS also executes service activation commands received from the aggregator or system operator. Summary Voltus EMS calculates available regulation capacity, prepares data for bidding, and interfaces with trading systems or aggregators. The formal market bidding process remains the responsibility of the aggregator or market operator. However EMS/SCADA system can be expanded with such functionalities on request |
| 8.4 | Automatic bid submission | VOLTUS INPUT REQUIRED | Question for Voltus: Can the EMS automatically submit bids to market/TSO platforms without manual intervention? (a) What market platforms are currently integrated? (b) Is this available for the Cyprus market (CERA/TSO)? (c) What is the failsafe if automatic submission fails? Voltus response: Voltus EMS is not a trading platform and does not normally perform formal market bid submission on its own. Market participation is typically handled by a dedicated trading system or an external aggregator. However, the EMS can operate in a fully automated data exchange mode, where all required operational data, availability profiles, and schedules are automatically transmitted to the trading system or aggregator responsible for submitting bids. There is possibility to expand Voltus EMS/SCADA system with functionalities like automatic bidding on request. (a) Currently integrated market platforms The EMS is not limited to a single specific market platform. Integration is implemented on a project-specific basis and may include: - trading system APIs, - aggregator platforms, - asset portfolio management or utility systems. The scope of integration depends on the project structure and local market environment. (b) Availability for the Cyprus market (CERA / TSO) The EMS architecture is designed to adapt to market rules and communication interfaces defined by the regulator or system operator. In the case of Cyprus, where the electricity market model is being developed by CERA / TSO, integration can be implemented once formal technical and communication requirements are defined. The system is prepared for such future integration. (c) Failsafe mechanisms in case of automatic transmission failure If automatic data transmission or submission fails, configurable fallback mechanisms may be applied, such as: - automatic retransmission attempts, - operator notification (SCADA alarm, SMS, email), - fallback to the last confirmed schedule or safe operating mode, - manual submission via the trading system or aggregator, - full logging and audit trail of communication attempts. Summary Voltus EMS does not directly submit market bids but enables fully automated cooperation with trading systems or aggregators that perform the bidding process. The Voltus SCADA system can be extended in the future to support the bidding process or — depending on market requirements and system integration — enable direct market bid submission. |

| 8.5 | TSO communication protocol compliance | CONFIRMED | Native IEC 60870-5-104 support (mandatory for Cyprus DSO/EAC): TCP/IP port 2404 RTU functionality integrated in WAGO PFC200 (PPC + RTU + IEC-104 gateway) Full signal point list confirmed (active power, reactive power, CB control, telemetry, protection signals) IEC-104 timing parameters configured per DSO requirements (t0=30s, t1=15s, t2=10s, t3=20s) Discrete curtailment levels: 100% / 60% / 30% / 0% Response time: Command acknowledgment <3s (target <500ms), power adjustment <60s (target <10s) |
| --- | --- | --- | --- |

- FORECAST INTEGRATION

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 9.1 | Price forecasting module | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS include a built-in electricity price forecasting module? (a) What data sources does it use? (b) What forecast horizons are supported (day-ahead, week-ahead)? (c) What is the forecast accuracy (MAPE)? (d) Is it pre-trained for the Cyprus market or does it require market-specific calibration? Voltus response: Voltus EMS does not include a universal, pre-trained electricity price forecasting module for all markets, as price models strongly depend on local market structures. The system uses available price forecasts (e.g. those published by market operators such as Nord Pool). If required, it can be integrated with external forecasting sources or equipped with a dedicated forecasting module. Price forecast data sources may include: - market data (day-ahead, intraday), - RES generation forecasts, - external forecasting services or trading systems. The EMS can retrieve forecasts via API or other integration interfaces. Summary Voltus EMS uses external electricity price forecasts and can integrate with forecasting systems. Dedicated forecasting models can be implemented and calibrated for specific markets — including Cyprus — based on local historical data. In the future, the SCADA system can be extended with its own electricity price forecasting functionality. |
| 9.2 | Volatility modelling | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS model price volatility for dispatch optimization? (a) Can it adjust bidding strategy based on expected price spreads? (b) Does it account for seasonal and intraday volatility patterns? (c) Can it identify high-value arbitrage windows dynamically? Voltus response: Voltus EMS does not use an advanced probabilistic price volatility model as a separate mathematical module by default. However, the system operationally analyzes price profiles and their variability for energy storage optimization and price arbitrage. (a) Strategy adjustment based on price spreads Yes. The EMS analyzes price differences over time and makes charging and discharging decisions accordingly. If expected price spreads are too small (e.g. insufficient to cover losses or operating costs), the system may suspend cycling and avoid arbitrage. (b) Seasonal and intraday patterns The EMS can account for recurring price patterns, such as: - intraday patterns, - predefined market profiles, - operating strategies based on schedules and historical data. The extent to which these patterns are considered depends on control logic configuration and data availability. (c) Dynamic identification of arbitrage windows Yes. The system automatically identifies favorable charging and discharging periods based on: - current or forecast prices, - available SOC operating range, - technical system constraints, - the active operating strategy. Arbitrage windows can be determined dynamically using rolling optimization. Summary Voltus EMS does not model price volatility probabilistically but operationally analyzes price spreads and patterns. The system adjusts operating strategy to price differences over time and dynamically identifies profitable arbitrage windows while respecting technical constraints and system configuration. |
| 9.3 | Load & RES forecast integration | VOLTUS INPUT REQUIRED | Question for Voltus: Can the EMS ingest external load and renewable energy (solar/wind) generation forecasts? (a) What input formats are supported (API, CSV, MQTT)? (b) Can it integrate with third-party forecast providers? (c) Is there a built-in solar generation forecast based on irradiance data? (d) How does the RES forecast influence dispatch decisions? Voltus response: Yes — Voltus EMS can use external forecasts of load and renewable energy generation (PV, wind) as inputs for system planning and operational optimization. (a) Supported input data formats The EMS supports standard data integration methods, including: - API (REST, web services), - CSV / Excel files, - MQTT, - Modbus TCP, - other project-specific communication protocols. The integration format depends on the data source and system architecture. (b) Integration with third-party forecast providers Yes. The EMS can integrate with external forecasting systems, weather data providers, trading platforms, or dedicated models for RES generation and load forecasting. Integration is implemented via API or data exchange according to project requirements. (c) Built-in solar generation forecast The EMS can use PV generation forecasts based on irradiance and weather data, if such data are available. Forecasts may be: - provided by external systems, or - generated locally using PV production models and meteorological data (if implemented as part of the project configuration). (d) Influence of RES forecasts on dispatch decisions RES forecasts are used in operational planning, including: - planning battery charging and discharging, - limiting export or preventing overloads, - reserving capacity for ancillary services, - optimizing self-consumption, - planning arbitrage strategies and operating schedules. Forecasts are incorporated into the optimization process (e.g. day-ahead or rolling horizon). Summary Voltus EMS can ingest external load and renewable generation forecasts, integrate with forecasting providers, and directly use these data in system optimization and operational planning. |
| 9.4 | Scenario-based planning | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS support scenario-based planning for dispatch strategy evaluation? (a) Can operators compare multiple dispatch strategies (e.g., aggressive cycling vs. conservative) before committing? (b) Are "what-if" simulations available? (c) Can scenarios include different price forecast assumptions? Voltus response: Yes — Voltus EMS supports scenario-based planning and evaluation of different operating strategies before operational decisions are implemented. (a) Comparing different dispatch strategies Yes. Operators can define and compare different dispatch strategies, for example: - aggressive cycling strategies, - conservative strategies (battery lifetime protection), - different SOC operating ranges, - different power limits or service priorities. Results can be evaluated in terms of energy flows, revenue, system utilization, or other operational metrics. (b) “What-if” simulations Yes. The system supports scenario-based (“what-if”) simulations that allow evaluation of how changes in parameters or operating conditions would affect system performance — without impacting real operation. Simulations can be performed within the SCADA environment or using dedicated analytical functions and scripts. (c) Different price forecast assumptions Yes. Scenarios can include different energy price assumptions, such as: - different price profiles, - high / medium / low price scenarios, - alternative forecasts from different providers, - modified arbitrage profitability thresholds. Summary Voltus EMS enables multi-scenario analysis, comparison of dispatch strategies, and “what-if” simulations using different technical and market assumptions. This allows operators to select the optimal strategy before applying it in real system operation. |
| 9.5 | Machine learning forecasting engine | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS use machine learning for any forecasting function (price, load, generation, degradation)? (a) What ML techniques are employed (LSTM, gradient boosting, ensemble)? (b) Is the model re-trained automatically as new data is collected? (c) What is the minimum data history required for model training? (d) Can model performance be audited by the client? Voltus response: Voltus EMS does not require machine learning models for standard system operation. Forecasting functions can be based on external data sources or classical analytical models. At the same time, the system architecture allows the implementation of ML models in areas such as electricity price forecasting, renewable generation forecasting, load prediction, or degradation analysis — if required by the project design. |

- CYBERSECURITY COMPLIANCE (IEC 62443)

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 10.1 | Role-based access control | CONFIRMED | RBAC implemented with multi-factor authentication (MFA) support. Defined security zones: Zone 1: Field devices (PCS, BMS) — Modbus TCP (encrypted tunnel) Zone 2: Local SCADA/EMS — Internal only Zone 3: DMZ (IEC-104 gateway) — IEC-104 to DSO Zone 4: Cloud/remote access — HTTPS/REST API VPN for remote access. Audit logging with 12-month minimum retention. |
| 10.2 | Network segmentation | CONFIRMED | OT/IT network separation implemented via 4-zone architecture (see 10.1). Industrial firewall (IEC 62443 certified) required per park. Managed switch with VLAN capability. DMZ between operational and enterprise networks. |
| 10.3 | Encrypted communication | CONFIRMED | TLS 1.3 minimum for all external communications TLS 1.2+ for SCADA communications Certificate-based authentication where supported Encrypted tunnel for Modbus TCP (Zone 1) IPSec/OpenVPN for remote access |
| 10.4 | Intrusion detection system | VOLTUS INPUT REQUIRED | Real-time connection monitoring is documented for DSO communication. Firewall with whitelist rules per DSO IP. Question for Voltus: Does the Voltus EMS or the recommended network architecture include an intrusion detection/prevention system (IDS/IPS)? (a) Is this network-based or host-based? (b) Does it monitor for OT-specific threats (e.g., Modbus protocol anomalies, unauthorized SCADA commands)? (c) Is it integrated with the SCADA alarm system? (d) Is it a Voltus-provided component or third-party? Voltus response: Voltus suggest to use Fortigate Firewalls which provides requestes IDS/IPS. Firewall healthstate is monitored by SCADA however not full scope of alarming is stored in SCADA itself |
| 10.5 | Secure firmware update | VOLTUS INPUT REQUIRED | Question for Voltus: What is the secure firmware/software update process for the WAGO PFC200 and Voltus EMS software? (a) Are updates cryptographically signed? (b) Is rollback supported if an update fails? (c) Can updates be staged and tested before fleet- wide deployment? (d) What is the typical update frequency? (e) Are security patches prioritized with SLA? Voltus response: The software update process for the WAGO PFC200 controller and the Voltus EMS system follows industrial cybersecurity best practices and formal change management procedures. Updates can be performed locally or remotely, depending on the project’s security policy. (a) Cryptographic signing of updates Yes — update package integrity is verified before installation. For third-party components (e.g. WAGO), manufacturer security mechanisms are applied. Voltus EMS packages are distributed in a controlled manner with source and integrity verification. (b) Rollback capability Yes — it is possible to revert to a previous software version if an update fails or if a stable configuration needs to be restored. The rollback scope depends on the system component and the applied update procedure. (c) Staged updates and testing before fleet-wide deployment Yes — updates can be deployed in stages, for example: - testing in a test environment or on a selected site, - pilot deployment, - full fleet-wide rollout after validation. This is standard practice for multi-site or critical installations. (d) Update frequency Updates are released as needed, including: - functional enhancements, - compatibility updates, - bug fixes, - security updates. There is no fixed release schedule — updates are issued in a controlled manner according to the product development cycle and project requirements. (e) Security patch prioritization and SLA Yes — security patches are treated with high priority. Response and deployment time depend on the severity of the vulnerability and the applicable SLA or service agreement. Critical security issues may trigger accelerated patch release and deployment. Summary Voltus EMS and WAGO controller updates are managed in a secure and controlled manner, including integrity verification, rollback capability, staged deployment, and prioritized handling of security patches in accordance with service agreements and project requirements. |
| 10.6 | Audit trail logging | CONFIRMED | All commands logged with timestamps. 12-month minimum retention. Curtailment event logging includes: timestamp (start/end UTC+2), command type (analog/discrete/CB trip), commanded vs. |

|  |  |  | achieved values, curtailed energy (kWh), response time, source identification (DSO/Protection/Auto). |
| --- | --- | --- | --- |

- REMOTE DISPATCH CAPABILITY

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 11.1 | Real-time dispatch override | CONFIRMED | DSO SCADA curtailment commands override market dispatch in real-time. Active power setpoint (Address 30) and discrete curtailment levels (100%/60%/30%/0%) can be commanded remotely. Command acknowledgment <3s (target <500ms). |
| 11.2 | TSO direct control interface | CONFIRMED | IEC 60870-5-104 native interface. Full signal point list: Active/reactive power setpoints and feedback Circuit breaker control (open/close) and status Curtailment level commands Telemetry (voltage, power, PF, availability) Protection signals (overcurrent, frequency, voltage, earth fault, ROCOF) |
| 11.3 | Manual override hierarchy | CONFIRMED 1 2 3 4 | Priority hierarchy (non-negotiable): . Protection (local firmware) — Cannot be overridden . DSO SCADA curtailment — Absolute priority over all dispatch . DSO CB control — Hard disconnect . Market dispatch / optimization — Only active when DSO not curtailing Local/remote mode selectable (Address 101: 0=Remote, 1=Local). |
| 11.4 | Fail-safe fallback logic | PARTIAL — VOLTUS INPUT REQUIRED | Confirmed local firmware fallback: LFSM-O (frequency-based): Automatic curtailment at 50.2–50.7 Hz, switch to charging at 50.7 Hz, disconnect >52 Hz or <47 Hz P(V) voltage-based: Automatic power adjustment at 1.07–1.10 pu Question for Voltus: What happens when EMS communication is lost? (a) Does the WAGO controller revert to a pre-programmed safe mode? (b) What is the communication loss detection timeout? (c) Can the fallback dispatch schedule be pre-loaded? (d) Is there a "last known good" state retention? (e) How is communication restoration handled (automatic or manual re-sync)? Voltus response: In the event of loss of supervisory communication (e.g. with EMS, SCADA, aggregator, or system operator), the system transitions to autonomous operation according to predefined local control and safety logic. The WAGO controller and field devices continue operating based on local parameters and protection mechanisms. (a) Safe mode upon communication loss Yes. The WAGO controller switches to a pre-programmed autonomous / safe operating mode, which may include: - maintaining the last valid setpoints, - switching to local power control mode, - executing a predefined operating strategy, - enforcing protection and grid response functions (e.g. LFSM-O, P(V), voltage and frequency limits). The exact behavior depends on project configuration. (b) Communication loss detection timeout The detection time depends on the communication protocol configuration and watchdog / heartbeat mechanisms. Typically, it ranges from a few seconds to several tens of seconds and is configurable according to project or system operator requirements. (c) Preloaded fallback dispatch schedule Yes. A fallback operating schedule or control strategy can be preloaded and automatically activated when supervisory communication is lost. This may include, for example: - fixed power profiles, - limited operation mode, - rule-based local control. (d) Last known good state retention Yes. The system can maintain the last validated and safe operating state (“last known good state”) and continue operating under those conditions until communication is restored or fallback logic is activated. (e) Communication restoration handling When communication is restored, automatic system resynchronization can be performed, including: - updating setpoints and schedules, - confirming device operational status, - returning to supervisory control. Depending on project configuration, this process can be fully automatic or require operator confirmation. Summary In case of communication loss, the system switches to autonomous operation using predefined control logic or a fallback schedule. The controller maintains the last safe operating state, and once communication is restored, the system can automatically resynchronize with supervisory control or require operator confirmation, depending on project configuration. |

- REDUNDANCY ARCHITECTURE

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 12.1 | Dual EMS servers | PARTIAL — VOLTUS INPUT REQUIRED | Confirmed: Linyang BAMS provides 2 redundant hosts per container for BMS management. Question for Voltus: What is the EMS server architecture for redundancy? (a) Is the SCADA Global deployed as dual-server (active/standby)? (b) If the primary EMS server fails, what is the failover time? (c) Is data synchronized between primary and standby servers? (d) For SCADA Local, is there any redundancy or is the WAGO PFC200 the single point of control? Voltus response: The Voltus EMS server architecture can be designed with redundancy, depending on the reliability requirements of the installation and the standards of the investor or system operator. Redundancy may cover SCADA Global, SCADA Local, and the underlying server infrastructure. (a) SCADA Global redundancy Yes — SCADA Global can be deployed in a redundant architecture, typically as a dual-server active/standby configuration. The standby server remains synchronized and ready to take over in the event of a primary server failure. (b) Failover time In the event of a primary server failure, automatic failover to the standby server is performed. Typical failover time ranges from a few seconds to several tens of seconds, depending on the IT infrastructure, monitoring mechanisms, and system configuration. (c) Data synchronization Yes — operational data, configuration, and databases are synchronized between the primary and standby servers to ensure continuity of operation and minimize data loss. The scope and method of synchronization depend on the deployment architecture (e.g. database replication, real-time synchronization). (d) SCADA Local / local control redundancy Local control performed by the WAGO PFC200 controller operates independently of SCADA Global and ensures continuous plant control. Typically, a single controller performs the local control function; however: - redundant PLC architectures can be implemented if required by the project, - protection and regulatory functions operate locally and independently of supervisory servers, - depending on project requirements, the WAGO PFC200 controller may interface with a local SCADA server (SCADA Local), which aggregates and archives plant data. SCADA Local may function as a local data repository and communication intermediary, with SCADA Global retrieving data from SCADA Local. In such architecture, SCADA Local acts as a local operational data backup. From a process control perspective, the local controller remains active even if supervisory systems are unavailable. Summary SCADA Global and, optionally, SCADA Local can be deployed in a redundant active/standby architecture with data synchronization and automatic failover. The local control layer based on the WAGO controller operates autonomously and ensures continuous plant operation regardless of supervisory system availability. |
| 12.2 | Redundant communication lines | PARTIAL — VOLTUS INPUT REQUIRED | Available communication options: M2M (2G/4G) via CYTA: ~50–200 ms latency E-Line (Ethernet P2P) via CYTA: <10 ms latency Fiber optic via EAC: <5 ms latency Question for Voltus: Does the EMS support automatic failover between communication paths (e.g., fiber primary, 4G backup)? (a) What is the failover detection time? (b) Is the switchover seamless or does it require re-establishment of IEC-104 connection? (c) Can both paths be active simultaneously (load balancing or hot standby)? Voltus response: Yes — Voltus EMS can operate with redundant communication paths, for example fiber as the primary link and 4G / M2M as the backup. Automatic failover depends on the configuration of the network infrastructure and communication devices. (a) Failure detection and failover time The detection time for communication loss depends on monitoring mechanisms (e.g. heartbeat, watchdog, VPN or IP monitoring). Typically: - failure detection: a few to several seconds, - switchover to backup link: automatic upon detection. (b) Switchover behavior The switchover behavior depends on the network architecture. In most standard configurations (e.g. change of WAN interface, IP address, or VPN tunnel), the communication session (e.g. IEC 60870-5-104 or TCP) is automatically re-established. In more advanced network architectures that preserve addressing or maintain session state, switchover may occur with little or no interruption to communication. The exact behavior depends on the project’s network configuration. (c) Parallel operation of communication paths Different redundancy modes are possible: - active / standby (most common), - parallel monitoring of both links, - load sharing / bonding (if supported by the infrastructure). Configuration depends on project design and system operator requirements. Summary Voltus EMS supports redundant communication paths with automatic failover in case of link failure. The switchover mechanism and continuity of communication sessions depend on the network architecture and communication infrastructure configuration. |
| 12.3 | Backup power supply | PARTIAL — VOLTUS INPUT REQUIRED | UPS for controls is listed as required hardware per park (Lighthief to procure). Question for Voltus: What are the UPS requirements for the WAGO PFC200 and EMS components? (a) What is the minimum runtime required (e.g., ride-through for grid fault vs. graceful shutdown)? (b) What is the power consumption of the WAGO controller + I/O modules? (c) Is there a recommended UPS specification? Voltus response: UPS for control systems ensures continuous operation of the controller, communications, and safe shutdown of systems in the event of power loss. Exact requirements depend on the installation architecture. (a) Minimum runtime Depends on the UPS function: - ride-through of short power interruptions: approx. 1–5 minutes, - controlled system shutdown (SCADA / IT): approx. 10–30 minutes, - longer durations — if required by project specifications. (b) Power consumption — WAGO PFC200 + I/O Typical values: - controller: 10–20 W, - I/O module: 1–2 W per module, - typical control cabinet: 20–60 W (excluding additional equipment). Routers, switches, and any local server should also be included in the load calculation. (c) Recommended UPS type An industrial online (double conversion) UPS is recommended, with: - appropriate backup runtime, - battery monitoring and alarms, - communication capability (optional Modbus / SNMP), - safe shutdown functionality for IT systems. Summary: The UPS is sized based on actual power consumption and required runtime to ensure continuous control operation and safe system shutdown. |
| 12.4 | Hot-standby failover | VOLTUS INPUT REQUIRED | Question for Voltus: Is hot-standby failover supported at any level of the EMS architecture? (a) WAGO controller level: is dual-PLC supported? (b) SCADA Local level: active/standby? (c) SCADA Global level: active/standby with automatic failover? (d) What is the RTO (recovery time objective) for each level? Voltus response: Yes — the Voltus EMS architecture can support hot-standby failover at different system levels. The scope of redundancy depends on project requirements and the selected infrastructure design. (a) WAGO controller level (PLC) A single controller is typically used for local control functions. However, a dual-PLC redundant architecture can be implemented if high availability is required. Typical RTO: - single PLC: no failover (controller operates locally), - redundant PLC (if implemented): < 1–5 seconds (depending on configuration and synchronization). (b) SCADA Local level SCADA Local can be deployed in an active / standby configuration with real-time data synchronization if required by the project. In standard installations, a single local server may be used, with redundancy optional. Typical RTO: - single server: manual restart or recovery required, - active / standby: several to several tens of seconds. (c) SCADA Global level Yes — SCADA Global can be deployed in an active / standby architecture with automatic failover and synchronized data. Typical RTO: - automatic switchover: several to several tens of seconds, - dependent on IT infrastructure and monitoring mechanisms. |

| 12.5 | Edge controller fallback mode | PARTIAL — VOLTUS INPUT REQUIRED | Confirmed: WAGO PFC200 runs local firmware with automatic frequency-based (LFSM-O) and voltage-based (P(V)) curtailment, independent of EMS communication. Question for Voltus: Beyond protection-mode fallback, can the WAGO edge controller execute a pre-loaded dispatch schedule autonomously if cloud/central EMS connection is lost? (a) How long can it operate autonomously? (b) Can the fallback schedule be updated remotely before disconnection? (c) Does it log operations during autonomous mode for later sync? Voltus response: Whole schedule is being stored in Local SCADA so any connection loss to central/cloud SCADA is not harming system operatibility |
| --- | --- | --- | --- |

- DATA LOGGING RESOLUTION & KPI MONITORING

  - Data Logging Resolution

| # | Client Requirement | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 13.1a | Sub-second frequency data | PARTIAL — VOLTUS INPUT REQUIRED | BMS hardware samples at ≤100 ms (voltage/current) and ≤200 ms (temperature). EMS logs at 1-second resolution. Question for Voltus: Can the EMS log at sub-second resolution (e.g., 100 ms or 200 ms) for specific signals or during specific events? What is the storage impact and is this configurable per signal group? Voltus response: Frequency of polling data can not be determined in early stage of project. With a larger number of signals, there is a high risk of overloading communication with the device and disturbing readout or control performance. Achieving stable operation at such sampling rates is technically demanding and depends on the capabilities of the data source (e.g. BMS / PCS) and the communication channel. Therefore, the EMS typically operates using a hybrid approach: - signals are read cyclically (often every few seconds, depending on the device and priority), - based on these readings, the system calculates min / max / average values over a defined time window, - aggregated data are stored in the database at intervals such as 1 min / 5 min / 15 min, depending on signal type and configuration. All parameters are configurable — each signal or signal group may have a different sampling frequency and aggregation / storage interval. Very frequent data recording (especially sub-second logging) can significantly increase data volume and rapidly consume storage capacity. For this reason, high-resolution logging is typically applied selectively or triggered by specific events. |
| 13.1b | 1-minute settlement aggregation | CONFIRMED | Performance data at 1-minute resolution with 1-year full retention and 10-year aggregated retention. |
| 13.1c | Market bid archive | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS archive all market bid submissions and outcomes? (a) Are bids stored with timestamp, volume, price, and acceptance status? (b) What is the retention period for bid archives? (c) Can bid history be exported for audit/reconciliation? Voltus response: Voltus EMS can archive data related to system operating schedules, operational plans, and information exchanged with trading systems or aggregators. The scope of archiving depends on the market integration model and the role of the EMS in the bidding process. (a) Scope of archived data If the EMS generates or transmits bidding-related data, the system can store, for example: - timestamps, - power or energy volumes, - schedule parameters or recommendations, - data transmission status (e.g. sent / acknowledged — if available), - feedback from supervisory systems (if provided by the aggregator or market platform). The formal market acceptance status of bids depends on the trading system or aggregator and is archived in the EMS only if this information is returned to the system. (b) Data retention period The retention period for archived data is configurable and depends on project requirements, operator policies, or regulatory requirements. Typically, operational and planning data can be stored for multiple years (e.g. 3–10 years), provided sufficient archive storage capacity is available. (c) Data export for audit and reconciliation Yes — historical data can be exported for audit, reporting, or reconciliation purposes. Standard export formats include, for example: - CSV, - Excel, - API (e.g. JSON), - other formats required by external systems. Summary The EMS can archive bidding-related and operational scheduling data according to the scope of integration with trading systems or aggregators. The retention period is configurable, and data can be exported for audit and reconciliation purposes. |
| 13.1d | KPI dashboarding | CONFIRMED | Lighthief Master Dashboard provides portfolio-wide access across all groups. Consolidated alarms, performance reports, and aggregator access (read-only for ABIO, Synenergia). SCADA Global supports multi-park master dashboard capability. |
| 13.1e | Degradation tracking dashboard | VOLTUS INPUT REQUIRED | Question for Voltus: Is there a dedicated degradation tracking dashboard in the SCADA platform? (a) Does it display actual SOH vs. warranty curve? (b) Does it show cycle count, throughput, and calendar aging breakdown? (c) Is it available at container, park, and portfolio level? (d) Can it generate degradation reports for warranty claims? Voltus response: Voltus response Yes — the Voltus SCADA platform can provide a dedicated battery degradation monitoring dashboard. The scope and level of detail depend on the data available from the BMS and the configuration of the analytical layer. (a) SOH vs. warranty curve Yes — the dashboard can display: - actual SOH values reported by the BMS (historical and current), - reference or warranty curves defined by the OEM, - comparison of measured degradation versus expected performance. Visualization and comparison logic are configurable. (b) Cycle count, throughput, and calendar aging Yes — the system can present key operational indicators related to degradation, including: - equivalent cycle count (if calculated or provided), - cumulative energy throughput (charge / discharge), - operating time and usage history, - trend-based indicators related to calendar aging. If required, cycle aging and calendar aging can be presented separately, depending on the available data and configured analytical model. (c) Multi-level visibility Yes — degradation monitoring can be displayed at multiple aggregation levels, for example: - container / rack / system level, - site or park level, - portfolio or fleet level (multi-site monitoring). Aggregation and comparison across assets are supported. (d) Reporting for warranty and technical analysis Yes — the system can generate degradation reports for technical review, performance verification, and warranty support. Reports may include: - SOH trends over time, - comparison with warranty thresholds, - operating history and utilization metrics, - exported datasets for external analysis. Report structure and format are configurable. Summary Voltus SCADA can provide configurable degradation monitoring dashboards and reporting tools, using BMS data and operational history to visualize performance, compare against warranty expectations, and support technical and warranty-related analysis. |

  - KPI Monitoring

| # | KPI | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 13.2a | Availability (%) | CONFIRMED | Tracked. Warranty requires ≥97% availability. Address 505 reports PV Plant Availability in real-time telemetry. Monthly performance reports include availability metrics. |

| 13.2b | Round-trip efficiency (%) | CONFIRMED | System-level RTE specified at ≥86.06%. Monitored via energy metering (grid-side and BESS-side meters). Includes PCS conversion losses, auxiliary consumption, and thermal management loads. |
| --- | --- | --- | --- |
| 13.2c | Revenue per MW | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS/SCADA dashboard calculate and display revenue per MW as a standard KPI? Can it break down revenue by source (arbitrage, FCR, aFRR, curtailment avoidance)? Is this available at park and portfolio level? Voltus response: Yes such KPIs can be calculated.All required data needed for this purpose shall be delivered by customer as well as appropriate equations based on which such results can be obtained |
| 13.2d | Degradation cost per MWh | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS calculate degradation cost per MWh dispatched? (a) What cost model is used (replacement cost / cycle life, or incremental capacity loss valuation)? (b) Is this factored into dispatch optimization decisions? (c) Is it displayed as a KPI in the dashboard? Voltus response: Way of calculatins such KPI can be achieved in different ways. All required data needed for this purpose shall be delivered by customer as well as appropriate equations based on which such results can be obtained |
| 13.2e | Response time compliance | CONFIRMED | Tracked in curtailment event logging: response time per command recorded, measured against DSO requirements (<3s acknowledgment, <60s power adjustment). Voltus targets: <500ms acknowledgment, <10s power adjustment. |
| 13.2f | State-of-charge accuracy drift | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS monitor SOC estimation accuracy over time (drift detection)? (a) Is there a periodic SOC recalibration routine (e.g., full charge to known OCV)? (b) Can SOC drift be alarmed when it exceeds a threshold? (c) Is the SOC drift tracked as a KPI? Voltus response: EMS is not able to calculate SOC drift as data needed for this purpose are not achievable from BMS |
| 13.2g | Auxiliary consumption ratio | PARTIAL — VOLTUS INPUT REQUIRED | Auxiliary consumption specified at ≤2.5% of rated energy capacity. Includes HVAC, BMS, fire system, lighting, and controls. Question for Voltus: Is auxiliary consumption ratio tracked as a real- time KPI in the dashboard? Can it be broken down by subsystem (cooling vs. controls vs. fire system)? Is there alerting for auxiliary consumption exceeding normal range? Voltus response: There are no enough data from BMS to calculate energy usage per system therefore EMS is not able to calculate such KPI |

- ADDITIONAL CONSIDERATIONS

The client has specifically asked whether the following are taken into consideration and/or included in the package offer:

| # | Item | Status | Response / Voltus Input |
| --- | --- | --- | --- |
| 14.1 | Degradation-aware bidding logic | VOLTUS INPUT REQUIRED | Question for Voltus: Does the EMS incorporate battery degradation costs into market bidding decisions? (a) Can it set a minimum bid price that covers the degradation cost of the dispatch? (b) Can it refuse to bid into low-value markets when degradation cost exceeds revenue? (c) Is this configurable per asset owner's risk preferences? Voltus response: es — Voltus EMS can account for battery degradation effects in the economic assessment of energy storage operation and in operational recommendations. The scope of this functionality depends on system configuration and the optimization model implemented in the project. (a) Minimum bid price including degradation cost Yes — a degradation cost (e.g. expressed in financial units per MWh or per cycle) can be defined and included in the economic evaluation of system operation. Based on this, the EMS can determine minimum price levels or economic conditions under which dispatch is considered justified. (b) Limiting operation when not economically justified Yes — the system can limit or avoid operation (e.g. arbitrage or participation in specific services) if the expected revenue does not cover operational costs, including degradation costs. In practice, this allows the system to avoid low-margin or uneconomic operating cycles. (c) Configurable according to asset owner risk preferences Yes — economic parameters and optimization strategy can be configured according to investor or operator preferences, for example: - acceptable battery wear level, - degradation cost model, - revenue vs. asset lifetime priority, - conservative or aggressive operating strategy. Summary Voltus EMS can incorporate degradation costs into the economic evaluation of system operation and support decisions regarding minimum price thresholds and market participation. These parameters are configurable according to asset owner preferences and operational strategy. |
| 14.2 | Latency risk in ancillary markets | PARTIAL — VOLTUS INPUT REQUIRED | Communication latency options: Fiber (EAC): <5 ms — suitable for FCR (<1s target) E-Line (CYTA): <10 ms — suitable for FCR/aFRR M2M (4G): 50–200 ms — acceptable for aFRR, marginal for FCR Question for Voltus: How does the EMS handle latency risk for ancillary service delivery? (a) Is communication latency monitored in real-time? (b) Does the system pre-position (anticipatory dispatch) to compensate for communication delay? (c) Is there an alarm when measured latency exceeds the threshold for the active service type? (d) What is Voltus's recommendation for the primary communication path for ancillary services in Cyprus? Voltus response: Voltus EMS considers communication parameters in system monitoring and in assessing the ability to deliver ancillary services. Monitoring communication quality and stability is part of ensuring the required response dynamics. (a) Communication latency monitoring Yes — the system monitors communication status as well as connection availability and quality (e.g. response time, packet loss, session stability — depending on infrastructure and protocols). This information can be displayed in SCADA and used for diagnostics and to assess system readiness for providing regulation services. (b) Latency compensation (pre-positioning) Ancillary service control is primarily executed locally, at the controller and field device level, in accordance with the requirements of the specific service (e.g. frequency regulation). As a result, response to system signals does not rely solely on supervisory communication latency. The EMS may also apply operational strategies to ensure sufficient reserve availability and operating margins (e.g. maintaining appropriate SOC levels), supporting fast response capability. (c) Alarming when latency thresholds are exceeded Yes — communication quality thresholds appropriate for the active ancillary service can be defined. If configured limits are exceeded, the system can generate diagnostic or operational alarms and indicate the risk of non-compliance with service requirements. (d) Recommended communication path for ancillary services in Cyprus For services requiring very fast response (e.g. FCR), Voltus recommends communication links with very low latency and high stability, in particular: - fiber optic as the primary connection, - dedicated operator-grade communication links with guaranteed quality parameters. Mobile links (e.g. 4G / M2M) may be used as backup or for services with lower dynamic requirements (e.g. aFRR), depending on project conditions and system operator requirements. Summary Voltus EMS monitors communication quality, supports maintaining operational readiness, and enables alarms when communication performance falls outside service requirements. For services requiring very low latency, fiber or equivalent dedicated high-quality communication links are recommended. |
| 14.3 | Communication failure scenarios | PARTIAL — VOLTUS INPUT REQUIRED | Confirmed fallback behaviour: WAGO local firmware provides autonomous protection response (LFSM-O frequency, P(V) voltage) independent of communication. Question for Voltus: Please describe the complete communication failure scenario handling: (a) EMS-to-site loss: What does the edge controller do? For how long? (b) Site-to- DSO loss: How is IEC-104 reconnection handled? (c) BMS-to- EMS loss: Can the PCS continue operating? (d) Multi-path failure: If all communication paths fail simultaneously? (e) What are the configurable timeouts before escalation at each level? Voltus response: The Voltus EMS is designed with a layered architecture in which protection functions and core control are executed locally, independent of supervisory communication. In the event of communication loss, each system layer transitions to autonomous operation according to predefined control and safety logic. (a) Loss of communication between EMS and site If communication with the supervisory EMS is lost: - the local controller (e.g. WAGO) continues autonomous operation, - the last valid setpoints are maintained or a predefined local operating strategy is activated (if configured), - regulatory and protection functions continue to operate normally (e.g. LFSM-O, P(V), operational limits), - the system may enter safe or fallback mode according to project configuration. Autonomous operation is not time-limited by the system — it continues until communication is restored or local conditions require intervention. (b) Loss of communication between site and DSO (IEC 60870-5-104) If the connection to the system operator is lost: - the IEC-104 connection is automatically monitored and restored via reconnect mechanisms, - reconnection attempts are performed automatically according to communication configuration, - local regulatory and protection functions continue autonomous operation, - once communication is restored, system states are synchronized and normal remote operation resumes. (c) Loss of communication between BMS and EMS If communication with the BMS is lost: - supervisory EMS control may be limited or suspended, depending on configuration, - the PCS / battery system continues operating according to local BMS control logic and protection mechanisms, - if the BMS maintains local control and safety supervision, operation can continue within safe limits, - the EMS may switch to limited control or monitoring mode. Exact behavior depends on the BMS–PCS–EMS integration architecture. (d) Simultaneous failure of all communication paths If all external communication paths fail: - the system operates entirely in local mode, - all local protection, regulation, and operational functions remain active, - a predefined fallback strategy or last safe setpoints are maintained, - the system may transition to limited operation or safe shutdown, depending on project configuration. (e) Configurable timeouts and escalation logic Communication loss detection times and escalation thresholds are configurable at multiple system levels, for example: - protocol communication timeouts (heartbeat, watchdog), - time to fallback activation, - timing of operational and service alarms, - escalation logic (e.g. alarm → limited operation → safe mode). Exact values depend on project requirements, system operator requirements, and communication configuration. Summary In the event of communication failure, Voltus EMS ensures safe continuous operation through autonomous local control and multi-level fallback logic. Communication links are automatically restored, and detection and escalation timings are configurable according to project and operator requirements. |
| 14.4 | Ownership clauses in EMS vendor contract | COMMERCIAL / LEGAL | This is a commercial/legal question that will be addressed in the EMS vendor contract between Lighthief and Voltus. Question for Voltus: For client transparency, please confirm: (a) |

|  |  |  | Who owns the operational data generated by the EMS? (b) Is the EMS software licensed or purchased? (c) What happens to EMS functionality if the Voltus service contract is not renewed? (d) Can the client/asset owner access all historical data in perpetuity? (e) Is there an escrow arrangement for the EMS source code? Voltus response: This matter is governed by the commercial agreement between the client and Voltus. The following outlines the standard principles typically applied in EMS projects. (a) Ownership of operational data Operational data generated by the installation and the EMS system are owned by the asset owner or end client, unless otherwise specified in the contract. Voltus may process the data only to the extent necessary to provide system services, maintenance, technical support, or analytics — in accordance with the contract terms and applicable data protection regulations. (b) EMS software access model The EMS software is typically provided under a licensing model, not as a transfer of software ownership. The scope of the license (e.g. duration, updates, technical support) is defined in the license or service agreement. (c) System functionality if the service agreement is not renewed If the service agreement expires, the core operational functions of the system remain active in accordance with the license terms. However, access to additional services may be limited or discontinued, such as: - software updates, - technical support, - functional development, - remote services or advanced analytics. The exact scope depends on the contractual terms. (d) Access to historical data The client or asset owner has access to historical data generated by the installation and stored in the system. Long-term data retention depends on the archiving infrastructure and data retention policy defined for the project. Data can be exported and archived by the asset owner in accordance with agreed procedures. (e) Source code escrow Voltus offers the option of establishing a source code escrow arrangement as a contractual option. In such a case: - the system source code is stored with a trusted, independent third party (e.g. a specialized escrow provider or legal firm), - the software provider (Voltus) deposits the source code into the escrow, - the code is securely stored by the independent entity, - the escrow agreement defines the conditions under which the code may be released to the client (e.g. specified contractual events or inability of the supplier to provide support). The scope of the deposit, release conditions, and access rights are defined individually in the contract. Summary Detailed provisions regarding data ownership, software licensing, system functionality after service termination, and any source code escrow arrangement are defined contractually. Typically, operational data belong to the asset owner, the EMS operates under a licensing model, and escrow may be implemented as an optional safeguard to ensure long-term system continuity. |
| --- | --- | --- | --- |

| 14.5 | Scalability beyond initial capacity | VOLTUS INPUT REQUIRED | Question for Voltus: How does the EMS handle capacity expansion? (a) Can additional containers be added to an existing site without full re-commissioning? (b) Is the WAGO PFC200 I/O capacity sufficient for site expansion (additional PCS/containers)? (c) What is the maximum number of PCS/containers a single WAGO controller can manage? (d) Does the SCADA license need to be upgraded for capacity additions? (e) What is the process and cost for scaling an existing EMS installation? Voltus response: Voltus EMS is designed as a scalable and modular system, enabling site expansion as battery container count or system capacity increases. Specific requirements depend on the project architecture and hardware and licensing configuration. (a) Adding additional containers to an existing site Yes — additional battery containers or PCS units can be added without full re-commissioning of the entire installation. Standard integration steps include: - configuration of communication with new devices, - signal mapping updates, - verification of control strategies and power limits, - integration testing of new components. This process represents system expansion rather than full re-commissioning. (b) Control architecture and controller capacity The system is designed with a distributed control architecture. Typically: - one local EMS controller manages 1–2 battery containers and one PCS, - a supervisory HPC controller oversees the entire system and reads data from all local EMS controllers, - operational and aggregated data are transmitted from each EMS controller directly to the database and local SCADA. This architecture enables linear scalability by adding additional control units. (c) Maximum number of PCS / containers There is no single centralized limit for the entire system, as capacity can be scaled by adding additional EMS controllers. Each EMS controller manages its assigned local units, while the supervisory HPC controller coordinates operation across the entire site. (d) SCADA license for expansion Site expansion may require a SCADA license upgrade if the number of connected devices, data points, or licensed system functions increases. The scope depends on the licensing model defined for the project. (e) Process and cost of scaling an existing EMS installation System expansion typically includes: - installation of additional EMS controllers for new units, - communication integration and control configuration, - updates to visualization and reporting, - license extension if required, - integration testing. The scope and cost depend on the number of new containers and PCS units and any architectural changes, and are defined on a project-specific basis. Summary Voltus EMS uses a distributed control architecture in which local controllers manage individual containers and PCS units, while a supervisory HPC controller coordinates system-wide operation. Data are aggregated and transmitted to SCADA and the database, enabling modular expansion without full system re-commissioning. |
| --- | --- | --- | --- |
| 14.6 | Cyber penetration testing certification | VOLTUS INPUT REQUIRED | NIS2 compliance is mandatory for grid connection. IEC 62443 certified hardware is required per our specification. Question for Voltus: (a) Has the Voltus EMS platform undergone independent penetration testing? (b) If so, by which firm and when was the last test? (c) Can results/certification be shared with the client (redacted if needed)? (d) Is periodic penetration testing included in the maintenance contract? (e) Does Voltus hold any cybersecurity certifications (ISO 27001, IEC 62443 SL certification)? Voltus response: Voltus EMS is designed and implemented in accordance with industrial OT/SCADA cybersecurity best practices and critical infrastructure requirements. Voltus designs its systems in line with industrial security standards (e.g. IEC 62443) and information security policies. The scope of formal audits and certifications depends on the specific project, client requirements, and deployment architecture. (a) Independent penetration testing Penetration testing may be performed as part of project deployments or security audits required by the investor, system operator, or IT/OT infrastructure integrator. The scope and frequency of testing depend on contractual requirements and the deployment environment. (b) Testing entity and timing of the latest audit Voltus is currently undergoing a new cybersecurity certification process. Upon completion, penetration testing will be conducted by an appropriate independent audit organization. Details regarding the testing entity and exact timelines will be provided after completion of the certification process, which is expected to take approximately three months. (c) Sharing results with the client Yes — penetration testing results or security audit reports may be shared with the client, subject to confidentiality agreements and security policies (e.g. redacted or summary versions where required). (d) Periodic testing under maintenance agreements Periodic security testing may be included in the service agreement or SLA if required by the client or system operator. The scope, frequency, and format of security audits are defined contractually. (e) Cybersecurity certifications The system architecture is designed in accordance with industrial security standards (e.g. IEC 62443) and information security policies. Hardware certification (e.g. components compliant with IEC 62443) and system requirements are implemented in accordance with project specifications. The scope of formal organizational or product certifications (e.g. ISO 27001, IEC 62443 Security Level) depends on certification status and project-specific requirements. Summary Voltus designs systems in accordance with recognized industrial cybersecurity standards, including IEC 62443. Penetration testing and certification are performed in line with project requirements. A certification process is currently underway, after which independent security testing will be conducted. Audit documentation can be shared with the client subject to confidentiality requirements. |

22 items (30%) can be fully answered from existing Linyang OEM specifications, EPC documentation, and confirmed system architecture.

17 items (23%) are partially answered with hardware/system-level confirmation, but require Voltus input on EMS software-specific features.

34 items (47%) require Voltus input — primarily EMS optimization algorithms, market integration, forecasting, and advanced analytics that are Voltus software capabilities.

RESPONSE SUMMARY

| Category | CONFIRMED | PARTIAL | VOLTUS REQUIRED | Total |
| --- | --- | --- | --- | --- |
| Cell-Level Monitoring | 3 | 1 | 2 | 6 |
| Degradation Analytics | 0 | 0 | 5 | 5 |
| Thermal & Safety | 3 | 2 | 0 | 5 |
| Fault Detection | 0 | 2 | 2 | 4 |
| Data Infrastructure | 3 | 1 | 1 | 5 |
| EMS Optimization | 0 | 1 | 4 | 5 |
| Market Integration | 1 | 1 | 3 | 5 |
| Forecast Integration | 0 | 0 | 5 | 5 |
| Cybersecurity (IEC 62443) | 4 | 0 | 2 | 6 |
| Remote Dispatch | 3 | 1 | 0 | 4 |
| Redundancy Architecture | 0 | 4 | 1 | 5 |
| Data Logging & KPIs | 5 | 2 | 5 | 12 |
| Additional Considerations | 0 | 2 | 4 | 6 |
| TOTAL | 22 | 17 | 34 | 73 |

- RESPONSE INSTRUCTIONS

Dear Voltus Team, please:

- Fill in the orange response fields throughout this document

- For features that are available: provide a brief technical description of how they work

- For features that are not currently available: state clearly and indicate if they are on the product roadmap (with estimated timeline)

- For features that could be added as customization: indicate scope and cost implications

Deadline: Tuesday 25 February 2026 EOD

Demo scheduled: Wednesday 26 February 2026

Please prioritize Sections 7 (EMS Optimization), 9 (Forecasting), and 14 (Additional Considerations) as these are the areas where the client will probe deepest.

Where relevant, reference specific SCADA screenshots or documentation that can be shared with the client during the Wednesday demo

Prepared by: Lighthief Cyprus Ltd

Subject: RFI - BMS Monitoring, EMS Optimization & Cybersecurity (LCY-RFI-VOLTUS-2026-003)

For: Voltus EMS Team

Classification: Confidential

Pages: For internal use and vendor response only Document Reference: LCY-RFI-VOLTUS-2026-003 | Version 1.0 |

20 February 2026