## desr
1、Physical layer communication port is Ethernet. 2、The protocol is modbus TCP. 3、Others act as the master, while EMS acts as the slave. 4、EMS default address is 192.168.2.136, port number is 502.

## remote indication
Hex Address | Decimal Address | Signal Name | Identifiers | Unit | Type
228 | 552 | Door Status | 03 | IO | uint16 | 1- Normal 0- Abnormal
229 | 553 | Water Immersion | 03 | IO | uint16 | 0- Normal 1- Abnormal
22A | 554 | Fire Protection | 03 | IO | uint16 | 1- Normal 0- Abnormal
22B | 555 | Grid Not Energized | 03 | PCS | uint16 | 0- Normal 1- Abnormal
22C | 556 | Grid Overvoltage | 03 | PCS | uint16 | 0- Normal 1- Abnormal
22D | 557 | Grid Undervoltage | 03 | PCS | uint16 | 0- Normal 1- Abnormal
22E | 558 | Grid Overfrequency | 03 | PCS | uint16 | 0- Normal 1- Abnormal
22F | 559 | Grid Underfrequency | 03 | PCS | uint16 | 0- Normal 1- Abnormal
230 | 560 | Grid Phase Sequence Error | 03 | PCS | uint16 | 0- Normal 1- Abnormal
231 | 561 | Grid Phase Loss | 03 | PCS | uint16 | 0- Normal 1- Abnormal
232 | 562 | Grid Voltage Imbalance | 03 | PCS | uint16 | 0- Normal 1- Abnormal
233 | 563 | Grid Islanding Condition | 03 | PCS | uint16 | 0- Normal 1- Abnormal
234 | 564 | High Voltage Ride-through Protection | 03 | PCS | uint16 | 0- Normal 1- Abnormal
235 | 565 | Low Voltage Ride-through Protection | 03 | PCS | uint16 | 0- Normal 1- Abnormal
236 | 566 | Module Hardware Overcurrent | 03 | PCS | uint16 | 0- Normal 1- Abnormal
237 | 567 | Wave-by-Wave Current Limit Exceeded | 03 | PCS | uint16 | 0- Normal 1- Abnormal
238 | 568 | Busbar Hardware Overvoltage | 03 | PCS | uint16 | 0- Normal 1- Abnormal
239 | 569 | Power Supply Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
23A | 570 | Battery Current Hardware Overcurrent | 03 | PCS | uint16 | 0- Normal 1- Abnormal
23B | 571 | BMS Communication Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
23C | 572 | EMS Communication Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
23D | 573 | Slave Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
23E | 574 | Carrier Synchronization Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
23F | 575 | Master Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
240 | 576 | Master Communication Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
241 | 577 | Slave Communication Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
242 | 578 | STS Communication Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
243 | 579 | Grid-tied/Off-grid Switching Command Abnormal | 03 | PCS | uint16 | 0- Normal 1- Abnormal
244 | 580 | STS Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
245 | 581 | Pre-charge Timeout | 03 | PCS | uint16 | 0- Normal 1- Abnormal
246 | 582 | Busbar Overvoltage | 03 | PCS | uint16 | 0- Normal 1- Abnormal
247 | 583 | Busbar Undervoltage | 03 | PCS | uint16 | 0- Normal 1- Abnormal
248 | 584 | Positive/Negative Busbar Imbalance | 03 | PCS | uint16 | 0- Normal 1- Abnormal
249 | 585 | Busbar Short Circuit | 03 | PCS | uint16 | 0- Normal 1- Abnormal
24A | 586 | Busbar Voltage Detection Abnormal | 03 | PCS | uint16 | 0- Normal 1- Abnormal
24B | 587 | Positive/Negative Busbar to Ground Imbalance | 03 | PCS | uint16 | 0- Normal 1- Abnormal
24C | 588 | DC System Pre-charge Not Ready | 03 | PCS | uint16 | 0- Normal 1- Abnormal
24D | 589 | DC Power Supply Not Ready | 03 | PCS | uint16 | 0- Normal 1- Abnormal
24E | 590 | Battery Voltage Detection Abnormal | 03 | PCS | uint16 | 0- Normal 1- Abnormal
24F | 591 | Battery Voltage Polarity Reverse Connection Detection Abnormal | 03 | PCS | uint16 | 0- Normal 1- Abnormal
250 | 592 | Battery Overvoltage | 03 | PCS | uint16 | 0- Normal 1- Abnormal
251 | 593 | Battery Undervoltage | 03 | PCS | uint16 | 0- Normal 1- Abnormal
252 | 594 | Battery Overcurrent | 03 | PCS | uint16 | 0- Normal 1- Abnormal
253 | 595 | Module Overcurrent | 03 | PCS | uint16 | 0- Normal 1- Abnormal
254 | 596 | Grid-side Leakage Current Too Large | 03 | PCS | uint16 | 0- Normal 1- Abnormal
255 | 597 | Grid-side Module Current Imbalance | 03 | PCS | uint16 | 0- Normal 1- Abnormal
256 | 598 | Module I2t Overload | 03 | PCS | uint16 | 0- Normal 1- Abnormal
257 | 599 | Module Overtemperature | 03 | PCS | uint16 | 0- Normal 1- Abnormal
258 | 600 | Filter Capacitor Overvoltage | 03 | PCS | uint16 | 0- Normal 1- Abnormal
259 | 601 | Filter Capacitor Undervoltage | 03 | PCS | uint16 | 0- Normal 1- Abnormal
25A | 602 | Debugging Error | 03 | PCS | uint16 | 0- Normal 1- Abnormal
25B | 603 | Active Power Too Large | 03 | PCS | uint16 | 0- Normal 1- Abnormal
25C | 604 | Active Power Reaches Limit | 03 | PCS | uint16 | 0- Normal 1- Abnormal
25D | 605 | Overload Reduction Due to Overtemperature | 03 | PCS | uint16 | 0- Normal 1- Abnormal
25E | 606 | AC/DC Power Mismatch | 03 | PCS | uint16 | 0- Normal 1- Abnormal
25F | 607 | Large Deviation in Active Power | 03 | PCS | uint16 | 0- Normal 1- Abnormal
260 | 608 | Active Power Regulation Output Reaches Limit | 03 | PCS | uint16 | 0- Normal 1- Abnormal
261 | 609 | Reactive Power Regulation Output Reaches Limit | 03 | PCS | uint16 | 0- Normal 1- Abnormal
262 | 610 | Reactive Power Reaches Limit | 03 | PCS | uint16 | 0- Normal 1- Abnormal
263 | 611 | AC Lightning Protector Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
264 | 612 | DC Lightning Protector Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
265 | 613 | Internal Fan Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
266 | 614 | External Fan Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
267 | 615 | Emergency Shutdown | 03 | PCS | uint16 | 0- Normal 1- Abnormal
268 | 616 | Leakage Current Sensor Self-test Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
269 | 617 | DC Ground Insulation Impedance Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
26A | 618 | Excessive Leakage Current Zero Drift Sampling | 03 | PCS | uint16 | 0- Normal 1- Abnormal
26B | 619 | Internal Ambient Temperature Too High | 03 | PCS | uint16 | 0- Normal 1- Abnormal
26C | 620 | Excessive AD Sampling Zero Drift | 03 | PCS | uint16 | 0- Normal 1- Abnormal
26D | 621 | AC Ground Insulation Fault | 03 | PCS | uint16 | 0- Normal 1- Abnormal
26E | 622 | Pre-charge Contactor Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
26F | 623 | Main Contactor Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
270 | 624 | DC Pre-charge Contactor Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
271 | 625 | DC Main Contactor Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
272 | 626 | Grid-tied Contactor Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
273 | 627 | BMS Failure | 03 | PCS | uint16 | 0- Normal 1- Abnormal
274 | 628 | Charging Terminated | 03 | PCS | uint16 | 0- Normal 1- Abnormal
275 | 629 | Discharging Terminated | 03 | PCS | uint16 | 0- Normal 1- Abnormal
276 | 630 | Total Voltage Overvoltage Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
277 | 631 | Total Voltage Undervoltage Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
278 | 632 | Cell Overvoltage Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
279 | 633 | Cell Undervoltage Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
27A | 634 | Discharge Overcurrent Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
27B | 635 | Charge Overcurrent Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
27C | 636 | Discharge Battery Overtemperature Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
27D | 637 | Discharge Battery Undertemperature Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
27E | 638 | Charge Battery Overtemperature Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
27F | 639 | Charge Battery Undertemperature Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
280 | 640 | Insulation Resistance Too Low Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
281 | 641 | Terminal Temperature Too High Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
282 | 642 | High Voltage Box Connector Temperature Too High Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
283 | 643 | Cell Voltage Difference Too High Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
284 | 644 | Cell Temperature Difference Too High Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
285 | 645 | SOC Low Level 3 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
286 | 646 | Total Voltage Overvoltage Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
287 | 647 | Total Voltage Undervoltage Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
288 | 648 | Cell Overvoltage Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
289 | 649 | Cell Undervoltage Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
28A | 650 | Discharge Overcurrent Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
28B | 651 | Charge Overcurrent Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
28C | 652 | Discharge Battery Overtemperature Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
28D | 653 | Discharge Battery Undertemperature Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
28E | 654 | Charge Battery Overtemperature Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
28F | 655 | Charge Battery Undertemperature Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
290 | 656 | Insulation Resistance Too Low Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
291 | 657 | Terminal Temperature Too High Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
292 | 658 | High Voltage Box Connector Temperature Too High Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
293 | 659 | Cell Voltage Difference Too High Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
294 | 660 | Cell Temperature Difference Too High Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
295 | 661 | SOC Low Level 2 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
296 | 662 | Total Voltage Overvoltage Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
297 | 663 | Total Voltage Undervoltage Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
298 | 664 | Cell Overvoltage Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
299 | 665 | Cell Undervoltage Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
29A | 666 | Discharge Overcurrent Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
29B | 667 | Charge Overcurrent Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
29C | 668 | Discharge Battery Overtemperature Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
29D | 669 | Discharge Battery Undertemperature Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
29E | 670 | Charge Battery Overtemperature Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
29F | 671 | Charge Battery Undertemperature Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A0 | 672 | Insulation Resistance Too Low Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A1 | 673 | Terminal Temperature Too High Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A2 | 674 | High Voltage Box Connector Temperature Too High Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A3 | 675 | Cell Voltage Difference Too High Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A4 | 676 | Cell Temperature Difference Too High Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A5 | 677 | SOC Low Level 1 Alarm | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A6 | 678 | BMU Hardware Failure | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A7 | 679 | BCU Hardware Failure | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A8 | 680 | Fuse Failure | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2A9 | 681 | Contactor Sticking Failure | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2AA | 682 | BMU Communication Failure | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2AB | 683 | BAU Communication Failure | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2AC | 684 | Current Sensor Failure | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2AD | 685 | Insulation Monitoring Equipment Failure | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2AE | 686 | Disconnect Switch Unexpectedly Open | 03 | BMS | uint16 | 0- Normal 1- Abnormal
2AF | 687 | BMU1 Ejection Status | 03 | BMS | uint16 | 0-Not ejected 1- ejected
2B0 | 688 | BMU2 Ejection Status | 03 | BMS | uint16 | 0-Not ejected 1- ejected
2B1 | 689 | BMU3 Ejection Status | 03 | BMS | uint16 | 0-Not ejected 1- ejected
2B2 | 690 | BMU4 Ejection Status | 03 | BMS | uint16 | 0-Not ejected 1- ejected
2B3 | 691 | BMU5 Ejection Status | 03 | BMS | uint16 | 0-Not ejected 1- ejected
2B4 | 692 | BMU6 Ejection Status | 03 | BMS | uint16 | 0-Not ejected 1- ejected
2B5 | 693 | Battery Pack Fire Sprinkler Status | 03 | BMS | uint16 | 0-Not ejected 1- ejected
2B6 | 694 | TMS K1 High Voltage Relay Status | 03 | TMS | uint16 | 0- Open 1- Closed
2B7 | 695 | TMS K2 High Voltage Relay Status | 03 | TMS | uint16 | 0- Open 1- Closed
2B8 | 696 | Preheat Mode Feedback | 03 | TMS | uint16 | 0-Exit preheat mode 1- Switch to preheat mode
2B9 | 697 | TMS Failure Status | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2BA | 698 | PTC Temperature Switch Status | 03 | TMS | uint16 | 0- Open 1- Closed
2BB | 699 | Water Pump Switch | 03 | TMS | uint16 | 0- Open 1- Closed
2BC | 700 | Communication Loss Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2BD | 701 | High Voltage Relay 1 Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2BE | 702 | High Voltage Relay 2 Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2BF | 703 | ACDC1 Overvoltage Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C0 | 704 | ACDC1 Undervoltage Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C1 | 705 | ACDC2 Overvoltage Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C2 | 706 | ACDC2 Undervoltage Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C3 | 707 | Fan Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C4 | 708 | High Pressure Sensor Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C5 | 709 | High Pressure Too High | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C6 | 710 | Low Pressure Sensor Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C7 | 711 | Low Pressure Too Low | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C8 | 712 | Outlet Water Temperature Sensor Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2C9 | 713 | Inlet Water Temperature Sensor Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2CA | 714 | Water Pump Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2CB | 715 | Inlet Pressure Sensor Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2CC | 716 | Ambient Temperature Sensor Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2CD | 717 | Compressor Communication Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2CE | 718 | Compressor Controller Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2CF | 719 | PTC Overtemperature Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2D0 | 720 | Outlet Pressure Sensor Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2D1 | 721 | Water Pressure Difference Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2D2 | 722 | High Voltage Switch Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2D3 | 723 | Water Valve Failure 1 | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2D4 | 724 | Water Valve Failure 2 | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2D5 | 725 | Water Valve Failure 3 | 03 | TMS | uint16 | 0- Normal 1- Abnormal
2D6 | 726 | Exhaust Temperature Sensor Failure | 03 | TMS | uint16 | 0- Normal 1- Abnormal

## remote metering
Hex Address | Decimal Address | Signal Name | Identifiers | ratio | Unit | source | Type
1 | 1 | Operation Mode | 03 | 1 |  | SYS |  | 1-Manual Mode 2-Scheduled Mode
2 | 2 | Operating Status | 03 | 1 |  | SYS | uint16 | 0- Unknown 1- Shutdown 2- Standby 3- Charging 4- Discharging
3 | 3 | Rated Power | 03 | 0.1 | Kw | PCS | int16
4 | 4 | Rated Voltage | 03 | 0.1 | V | PCS | int16
5 | 5 | Rated Current | 03 | 0.1 | A | PCS | int16
6 | 6 | Rated Frequency | 03 | 0.1 | Hz | PCS | int16
7 | 7 | System Status | 03 | 1 |  | PCS | uint16 | Bit0: Initialization Bit1: Self-test Bit2: Ready to Operate Bit3: Grid-connected Operation Bit4: Charging Operation Bit5: Discharging Operation Bit6: Off-grid Operation Bit7: Fault Bit8: Charging Prohibited Bit9: Discharging Prohibited Bit10-15: Reserved
8 | 8 | AC Line Voltage AB | 03 | 0.1 | V | PCS | int16
9 | 9 | AC Line Voltage BC | 03 | 0.1 | V | PCS | int16
A | 10 | AC Line Voltage CA | 03 | 0.1 | V | PCS | int16
B | 11 | A-phase Current | 03 | 0.1 | A | PCS | int16
C | 12 | B-phase Current | 03 | 0.1 | A | PCS | int16
D | 13 | C-phase Current | 03 | 0.1 | A | PCS | int16
E | 14 | Apparent Power | 03 | 0.1 | kW | PCS | int16
F | 15 | Active Power | 03 | 0.1 | kW | PCS | int16
10 | 16 | Reactive Power | 03 | 0.1 | kVar | PCS | int16
11 | 17 | Voltage Frequency | 03 | 0.1 | Hz | PCS | int16
12 | 18 | DC Voltage | 03 | 0.1 | V | PCS | int16
13 | 19 | DC Current | 03 | 0.1 | A | PCS | int16
14 | 20 | Module Temperature | 03 | 0.1 | ℃ | PCS | int16
15 | 21 | Daily Charged Energy | 03 | 1 | kWh | PCS | uint16
16 | 22 | Daily Discharged Energy | 03 | 1 | kWh | PCS | uint16
17 | 23 | Total Charged Energy | 03 | 0.1 | kWh | PCS | uint16 | Total charge = total charge Total charge low
18 | 24 | Low Total Charged Energy | 03 | 0.001 | MWh | PCS | uint16
19 | 25 | Total Discharged Energy | 03 | 0.1 | kWh | PCS | uint16 | Total discharge = total discharge Total discharge Low total discharge
1A | 26 | Low Total Discharged Energy | 03 | 0.001 | MWh | PCS | uint16
1B | 27 | System Operating Status | 03 | 1 |  | PCS | uint16 | 0- Shutdown 1- Standby 2- Discharging Operation 3- Charging Operation 4- Zero-Power Operation
1C | 28 | Fault Status | 03 | 1 |  | PCS | uint16 | 0- Normal 1- Fault
1D | 29 | Power Factor | 03 | 0.1 |  | PCS | uint16
1E | 30 | System Status | 03 | 1 |  | BMS | uint16 | 0- Normal 1- Charging Prohibited 2- Discharging Prohibited 3- Standby 4- Shutdown
1F | 31 | Cluster Operational Status Indicator | 03 | 1 |  | BMS
20 | 32 | Charging Current Limit | 03 | 0.1 | A | BMS | uint16
21 | 33 | Discharging Current Limit | 03 | 0.1 | A | BMS | uint16
22 | 34 | Full Charge/Empty Status | 03 | 1 |  | BMS
23 | 35 | Total Voltage | 03 | 0.1 | V | BMS | uint16
24 | 36 | Total Current | 03 | 0.1 | A | BMS | uint16
25 | 37 | State of Charge (SOC) | 03 | 0.1 | % | BMS | uint16
26 | 38 | State of Health (SOH) | 03 | 1 | % | BMS | uint16
27 | 39 | Single Charge Capacity | 03 | 1 | kWh | BMS | uint16
28 | 40 | Cumulative Charge Capacity | 03 | 1 | kWh | BMS | uint16
29 | 41 | Single Discharge Capacity | 03 | 1 | kWh | BMS | uint16
2A | 42 | Cumulative Discharge Capacity | 03 | 1 | kWh | BMS | uint16
2B | 43 | Cluster Chargeable Capacity | 03 | 1 | kWh | BMS | uint16
2C | 44 | Cluster Dischargeable Capacity | 03 | 1 | kWh | BMS | uint16
2D | 45 | Highest Voltage Cell Box Number | 03 | 1 |  | BMS
2E | 46 | Highest Voltage Cell Serial Number | 03 | 1 |  | BMS | uint16
2F | 47 | Highest Cell Voltage Value | 03 | 1 | mV | BMS | uint16
30 | 48 | Lowest Voltage Cell Number | 03 | 1 |  | BMS
31 | 49 | Lowest Voltage Cell Serial Number | 03 | 1 |  | BMS | uint16
32 | 50 | Lowest Cell Voltage Value | 03 | 1 | mV | BMS | uint16
33 | 51 | Maximum Cell Voltage Difference | 03 | 1 |  | BMS
34 | 52 | Maximum Voltage Difference Box Number | 03 | 1 |  | BMS
35 | 53 | Highest Temperature Cell Box Number | 03 | 1 |  | BMS
36 | 54 | Highest Temperature Cell Serial Number | 03 | 1 |  | BMS | uint16
37 | 55 | Highest Sampling Point Temperature | 03 | 1 | ℃ | BMS | uint16
38 | 56 | Lowest Temperature Cell Box Number | 03 | 1 |  | BMS
39 | 57 | Lowest Temperature Cell Serial Number | 03 | 1 |  | BMS | uint16
3A | 58 | Lowest Sampling Point Temperature | 03 | 1 | ℃ | BMS | uint16
3B | 59 | Maximum Temperature Difference | 03 | 1 |  | BMS
3C | 60 | Maximum Temperature Difference Box Number | 03 | 1 |  | BMS
3D | 61 | Level 1 Alarm | 03 | 1 |  | BMS | uint16 | Alarm code: The specific descriptions are explained in registers 630-645.Non-zero indicates an alarm
3E | 62 | Level 2 Alarm | 03 | 1 |  | BMS | uint16 | Alarm code: The specific descriptions are explained in registers 646-661.Non-zero indicates an alarm
3F | 63 | Level 3 Alarm | 03 | 1 |  | BMS | uint16 | Alarm code: The specific descriptions are explained in registers 662-677.Non-zero indicates an alarm
40 | 64 | Fault Status | 03 | 1 |  | BMS | uint16 | Fault code: Specific fault explanationsare reflected in registers 678-686. A non-zero value indicates a fault
41 | 65 | General Alarm Signal | 03 | 1 |  | BMS | int16
42 | 66 | Single Battery Voltage_0 | 03 | 1 | mV | BMS | int16
43 | 67 | Single Battery Voltage_1 | 03 | 1 | mV | BMS | int16
44 | 68 | Single Battery Voltage_2 | 03 | 1 | mV | BMS | int16
45 | 69 | Single Battery Voltage_3 | 03 | 1 | mV | BMS | int16
46 | 70 | Single Battery Voltage_4 | 03 | 1 | mV | BMS | int16
47 | 71 | Single Battery Voltage_5 | 03 | 1 | mV | BMS | int16
48 | 72 | Single Battery Voltage_6 | 03 | 1 | mV | BMS | int16
49 | 73 | Single Battery Voltage_7 | 03 | 1 | mV | BMS | int16
4A | 74 | Single Battery Voltage_8 | 03 | 1 | mV | BMS | int16
4B | 75 | Single Battery Voltage_9 | 03 | 1 | mV | BMS | int16
4C | 76 | Single Battery Voltage_10 | 03 | 1 | mV | BMS | int16
4D | 77 | Single Battery Voltage_11 | 03 | 1 | mV | BMS | int16
4E | 78 | Single Battery Voltage_12 | 03 | 1 | mV | BMS | int16
4F | 79 | Single Battery Voltage_13 | 03 | 1 | mV | BMS | int16
50 | 80 | Single Battery Voltage_14 | 03 | 1 | mV | BMS | int16
51 | 81 | Single Battery Voltage_15 | 03 | 1 | mV | BMS | int16
52 | 82 | Single Battery Voltage_16 | 03 | 1 | mV | BMS | int16
53 | 83 | Single Battery Voltage_17 | 03 | 1 | mV | BMS | int16
54 | 84 | Single Battery Voltage_18 | 03 | 1 | mV | BMS | int16
55 | 85 | Single Battery Voltage_19 | 03 | 1 | mV | BMS | int16
56 | 86 | Single Battery Voltage_20 | 03 | 1 | mV | BMS | int16
57 | 87 | Single Battery Voltage_21 | 03 | 1 | mV | BMS | int16
58 | 88 | Single Battery Voltage_22 | 03 | 1 | mV | BMS | int16
59 | 89 | Single Battery Voltage_23 | 03 | 1 | mV | BMS | int16
5A | 90 | Single Battery Voltage_24 | 03 | 1 | mV | BMS | int16
5B | 91 | Single Battery Voltage_25 | 03 | 1 | mV | BMS | int16
5C | 92 | Single Battery Voltage_26 | 03 | 1 | mV | BMS | int16
5D | 93 | Single Battery Voltage_27 | 03 | 1 | mV | BMS | int16
5E | 94 | Single Battery Voltage_28 | 03 | 1 | mV | BMS | int16
5F | 95 | Single Battery Voltage_29 | 03 | 1 | mV | BMS | int16
60 | 96 | Single Battery Voltage_30 | 03 | 1 | mV | BMS | int16
61 | 97 | Single Battery Voltage_31 | 03 | 1 | mV | BMS | int16
62 | 98 | Single Battery Voltage_32 | 03 | 1 | mV | BMS | int16
63 | 99 | Single Battery Voltage_33 | 03 | 1 | mV | BMS | int16
64 | 100 | Single Battery Voltage_34 | 03 | 1 | mV | BMS | int16
65 | 101 | Single Battery Voltage_35 | 03 | 1 | mV | BMS | int16
66 | 102 | Single Battery Voltage_36 | 03 | 1 | mV | BMS | int16
67 | 103 | Single Battery Voltage_37 | 03 | 1 | mV | BMS | int16
68 | 104 | Single Battery Voltage_38 | 03 | 1 | mV | BMS | int16
69 | 105 | Single Battery Voltage_39 | 03 | 1 | mV | BMS | int16
6A | 106 | Single Battery Voltage_40 | 03 | 1 | mV | BMS | int16
6B | 107 | Single Battery Voltage_41 | 03 | 1 | mV | BMS | int16
6C | 108 | Single Battery Voltage_42 | 03 | 1 | mV | BMS | int16
6D | 109 | Single Battery Voltage_43 | 03 | 1 | mV | BMS | int16
6E | 110 | Single Battery Voltage_44 | 03 | 1 | mV | BMS | int16
6F | 111 | Single Battery Voltage_45 | 03 | 1 | mV | BMS | int16
70 | 112 | Single Battery Voltage_46 | 03 | 1 | mV | BMS | int16
71 | 113 | Single Battery Voltage_47 | 03 | 1 | mV | BMS | int16
72 | 114 | Single Battery Voltage_48 | 03 | 1 | mV | BMS | int16
73 | 115 | Single Battery Voltage_49 | 03 | 1 | mV | BMS | int16
74 | 116 | Single Battery Voltage_50 | 03 | 1 | mV | BMS | int16
75 | 117 | Single Battery Voltage_51 | 03 | 1 | mV | BMS | int16
76 | 118 | Single Battery Voltage_52 | 03 | 1 | mV | BMS | int16
77 | 119 | Single Battery Voltage_53 | 03 | 1 | mV | BMS | int16
78 | 120 | Single Battery Voltage_54 | 03 | 1 | mV | BMS | int16
79 | 121 | Single Battery Voltage_55 | 03 | 1 | mV | BMS | int16
7A | 122 | Single Battery Voltage_56 | 03 | 1 | mV | BMS | int16
7B | 123 | Single Battery Voltage_57 | 03 | 1 | mV | BMS | int16
7C | 124 | Single Battery Voltage_58 | 03 | 1 | mV | BMS | int16
7D | 125 | Single Battery Voltage_59 | 03 | 1 | mV | BMS | int16
7E | 126 | Single Battery Voltage_60 | 03 | 1 | mV | BMS | int16
7F | 127 | Single Battery Voltage_61 | 03 | 1 | mV | BMS | int16
80 | 128 | Single Battery Voltage_62 | 03 | 1 | mV | BMS | int16
81 | 129 | Single Battery Voltage_63 | 03 | 1 | mV | BMS | int16
82 | 130 | Single Battery Voltage_64 | 03 | 1 | mV | BMS | int16
83 | 131 | Single Battery Voltage_65 | 03 | 1 | mV | BMS | int16
84 | 132 | Single Battery Voltage_66 | 03 | 1 | mV | BMS | int16
85 | 133 | Single Battery Voltage_67 | 03 | 1 | mV | BMS | int16
86 | 134 | Single Battery Voltage_68 | 03 | 1 | mV | BMS | int16
87 | 135 | Single Battery Voltage_69 | 03 | 1 | mV | BMS | int16
88 | 136 | Single Battery Voltage_70 | 03 | 1 | mV | BMS | int16
89 | 137 | Single Battery Voltage_71 | 03 | 1 | mV | BMS | int16
8A | 138 | Single Battery Voltage_72 | 03 | 1 | mV | BMS | int16
8B | 139 | Single Battery Voltage_73 | 03 | 1 | mV | BMS | int16
8C | 140 | Single Battery Voltage_74 | 03 | 1 | mV | BMS | int16
8D | 141 | Single Battery Voltage_75 | 03 | 1 | mV | BMS | int16
8E | 142 | Single Battery Voltage_76 | 03 | 1 | mV | BMS | int16
8F | 143 | Single Battery Voltage_77 | 03 | 1 | mV | BMS | int16
90 | 144 | Single Battery Voltage_78 | 03 | 1 | mV | BMS | int16
91 | 145 | Single Battery Voltage_79 | 03 | 1 | mV | BMS | int16
92 | 146 | Single Battery Voltage_80 | 03 | 1 | mV | BMS | int16
93 | 147 | Single Battery Voltage_81 | 03 | 1 | mV | BMS | int16
94 | 148 | Single Battery Voltage_82 | 03 | 1 | mV | BMS | int16
95 | 149 | Single Battery Voltage_83 | 03 | 1 | mV | BMS | int16
96 | 150 | Single Battery Voltage_84 | 03 | 1 | mV | BMS | int16
97 | 151 | Single Battery Voltage_85 | 03 | 1 | mV | BMS | int16
98 | 152 | Single Battery Voltage_86 | 03 | 1 | mV | BMS | int16
99 | 153 | Single Battery Voltage_87 | 03 | 1 | mV | BMS | int16
9A | 154 | Single Battery Voltage_88 | 03 | 1 | mV | BMS | int16
9B | 155 | Single Battery Voltage_89 | 03 | 1 | mV | BMS | int16
9C | 156 | Single Battery Voltage_90 | 03 | 1 | mV | BMS | int16
9D | 157 | Single Battery Voltage_91 | 03 | 1 | mV | BMS | int16
9E | 158 | Single Battery Voltage_92 | 03 | 1 | mV | BMS | int16
9F | 159 | Single Battery Voltage_93 | 03 | 1 | mV | BMS | int16
A0 | 160 | Single Battery Voltage_94 | 03 | 1 | mV | BMS | int16
A1 | 161 | Single Battery Voltage_95 | 03 | 1 | mV | BMS | int16
A2 | 162 | Single Battery Voltage_96 | 03 | 1 | mV | BMS | int16
A3 | 163 | Single Battery Voltage_97 | 03 | 1 | mV | BMS | int16
A4 | 164 | Single Battery Voltage_98 | 03 | 1 | mV | BMS | int16
A5 | 165 | Single Battery Voltage_99 | 03 | 1 | mV | BMS | int16
A6 | 166 | Single Battery Voltage_100 | 03 | 1 | mV | BMS | int16
A7 | 167 | Single Battery Voltage_101 | 03 | 1 | mV | BMS | int16
A8 | 168 | Single Battery Voltage_102 | 03 | 1 | mV | BMS | int16
A9 | 169 | Single Battery Voltage_103 | 03 | 1 | mV | BMS | int16
AA | 170 | Single Battery Voltage_104 | 03 | 1 | mV | BMS | int16
AB | 171 | Single Battery Voltage_105 | 03 | 1 | mV | BMS | int16
AC | 172 | Single Battery Voltage_106 | 03 | 1 | mV | BMS | int16
AD | 173 | Single Battery Voltage_107 | 03 | 1 | mV | BMS | int16
AE | 174 | Single Battery Voltage_108 | 03 | 1 | mV | BMS | int16
AF | 175 | Single Battery Voltage_109 | 03 | 1 | mV | BMS | int16
B0 | 176 | Single Battery Voltage_110 | 03 | 1 | mV | BMS | int16
B1 | 177 | Single Battery Voltage_111 | 03 | 1 | mV | BMS | int16
B2 | 178 | Single Battery Voltage_112 | 03 | 1 | mV | BMS | int16
B3 | 179 | Single Battery Voltage_113 | 03 | 1 | mV | BMS | int16
B4 | 180 | Single Battery Voltage_114 | 03 | 1 | mV | BMS | int16
B5 | 181 | Single Battery Voltage_115 | 03 | 1 | mV | BMS | int16
B6 | 182 | Single Battery Voltage_116 | 03 | 1 | mV | BMS | int16
B7 | 183 | Single Battery Voltage_117 | 03 | 1 | mV | BMS | int16
B8 | 184 | Single Battery Voltage_118 | 03 | 1 | mV | BMS | int16
B9 | 185 | Single Battery Voltage_119 | 03 | 1 | mV | BMS | int16
BA | 186 | Single Battery Voltage_120 | 03 | 1 | mV | BMS | int16
BB | 187 | Single Battery Voltage_121 | 03 | 1 | mV | BMS | int16
BC | 188 | Single Battery Voltage_122 | 03 | 1 | mV | BMS | int16
BD | 189 | Single Battery Voltage_123 | 03 | 1 | mV | BMS | int16
BE | 190 | Single Battery Voltage_124 | 03 | 1 | mV | BMS | int16
BF | 191 | Single Battery Voltage_125 | 03 | 1 | mV | BMS | int16
C0 | 192 | Single Battery Voltage_126 | 03 | 1 | mV | BMS | int16
C1 | 193 | Single Battery Voltage_127 | 03 | 1 | mV | BMS | int16
C2 | 194 | Single Battery Voltage_128 | 03 | 1 | mV | BMS | int16
C3 | 195 | Single Battery Voltage_129 | 03 | 1 | mV | BMS | int16
C4 | 196 | Single Battery Voltage_130 | 03 | 1 | mV | BMS | int16
C5 | 197 | Single Battery Voltage_131 | 03 | 1 | mV | BMS | int16
C6 | 198 | Single Battery Voltage_132 | 03 | 1 | mV | BMS | int16
C7 | 199 | Single Battery Voltage_133 | 03 | 1 | mV | BMS | int16
C8 | 200 | Single Battery Voltage_134 | 03 | 1 | mV | BMS | int16
C9 | 201 | Single Battery Voltage_135 | 03 | 1 | mV | BMS | int16
CA | 202 | Single Battery Voltage_136 | 03 | 1 | mV | BMS | int16
CB | 203 | Single Battery Voltage_137 | 03 | 1 | mV | BMS | int16
CC | 204 | Single Battery Voltage_138 | 03 | 1 | mV | BMS | int16
CD | 205 | Single Battery Voltage_139 | 03 | 1 | mV | BMS | int16
CE | 206 | Single Battery Voltage_140 | 03 | 1 | mV | BMS | int16
CF | 207 | Single Battery Voltage_141 | 03 | 1 | mV | BMS | int16
D0 | 208 | Single Battery Voltage_142 | 03 | 1 | mV | BMS | int16
D1 | 209 | Single Battery Voltage_143 | 03 | 1 | mV | BMS | int16
D2 | 210 | Single Battery Voltage_144 | 03 | 1 | mV | BMS | int16
D3 | 211 | Single Battery Voltage_145 | 03 | 1 | mV | BMS | int16
D4 | 212 | Single Battery Voltage_146 | 03 | 1 | mV | BMS | int16
D5 | 213 | Single Battery Voltage_147 | 03 | 1 | mV | BMS | int16
D6 | 214 | Single Battery Voltage_148 | 03 | 1 | mV | BMS | int16
D7 | 215 | Single Battery Voltage_149 | 03 | 1 | mV | BMS | int16
D8 | 216 | Single Battery Voltage_150 | 03 | 1 | mV | BMS | int16
D9 | 217 | Single Battery Voltage_151 | 03 | 1 | mV | BMS | int16
DA | 218 | Single Battery Voltage_152 | 03 | 1 | mV | BMS | int16
DB | 219 | Single Battery Voltage_153 | 03 | 1 | mV | BMS | int16
DC | 220 | Single Battery Voltage_154 | 03 | 1 | mV | BMS | int16
DD | 221 | Single Battery Voltage_155 | 03 | 1 | mV | BMS | int16
DE | 222 | Single Battery Voltage_156 | 03 | 1 | mV | BMS | int16
DF | 223 | Single Battery Voltage_157 | 03 | 1 | mV | BMS | int16
E0 | 224 | Single Battery Voltage_158 | 03 | 1 | mV | BMS | int16
E1 | 225 | Single Battery Voltage_159 | 03 | 1 | mV | BMS | int16
E2 | 226 | Single Battery Voltage_160 | 03 | 1 | mV | BMS | int16
E3 | 227 | Single Battery Voltage_161 | 03 | 1 | mV | BMS | int16
E4 | 228 | Single Battery Voltage_162 | 03 | 1 | mV | BMS | int16
E5 | 229 | Single Battery Voltage_163 | 03 | 1 | mV | BMS | int16
E6 | 230 | Single Battery Voltage_164 | 03 | 1 | mV | BMS | int16
E7 | 231 | Single Battery Voltage_165 | 03 | 1 | mV | BMS | int16
E8 | 232 | Single Battery Voltage_166 | 03 | 1 | mV | BMS | int16
E9 | 233 | Single Battery Voltage_167 | 03 | 1 | mV | BMS | int16
EA | 234 | Single Battery Voltage_168 | 03 | 1 | mV | BMS | int16
EB | 235 | Single Battery Voltage_169 | 03 | 1 | mV | BMS | int16
EC | 236 | Single Battery Voltage_170 | 03 | 1 | mV | BMS | int16
ED | 237 | Single Battery Voltage_171 | 03 | 1 | mV | BMS | int16
EE | 238 | Single Battery Voltage_172 | 03 | 1 | mV | BMS | int16
EF | 239 | Single Battery Voltage_173 | 03 | 1 | mV | BMS | int16
F0 | 240 | Single Battery Voltage_174 | 03 | 1 | mV | BMS | int16
F1 | 241 | Single Battery Voltage_175 | 03 | 1 | mV | BMS | int16
F2 | 242 | Single Battery Voltage_176 | 03 | 1 | mV | BMS | int16
F3 | 243 | Single Battery Voltage_177 | 03 | 1 | mV | BMS | int16
F4 | 244 | Single Battery Voltage_178 | 03 | 1 | mV | BMS | int16
F5 | 245 | Single Battery Voltage_179 | 03 | 1 | mV | BMS | int16
F6 | 246 | Single Battery Voltage_180 | 03 | 1 | mV | BMS | int16
F7 | 247 | Single Battery Voltage_181 | 03 | 1 | mV | BMS | int16
F8 | 248 | Single Battery Voltage_182 | 03 | 1 | mV | BMS | int16
F9 | 249 | Single Battery Voltage_183 | 03 | 1 | mV | BMS | int16
FA | 250 | Single Battery Voltage_184 | 03 | 1 | mV | BMS | int16
FB | 251 | Single Battery Voltage_185 | 03 | 1 | mV | BMS | int16
FC | 252 | Single Battery Voltage_186 | 03 | 1 | mV | BMS | int16
FD | 253 | Single Battery Voltage_187 | 03 | 1 | mV | BMS | int16
FE | 254 | Single Battery Voltage_188 | 03 | 1 | mV | BMS | int16
FF | 255 | Single Battery Voltage_189 | 03 | 1 | mV | BMS | int16
100 | 256 | Single Battery Voltage_190 | 03 | 1 | mV | BMS | int16
101 | 257 | Single Battery Voltage_191 | 03 | 1 | mV | BMS | int16
102 | 258 | Single Battery Voltage_192 | 03 | 1 | mV | BMS | int16
103 | 259 | Single Battery Voltage_193 | 03 | 1 | mV | BMS | int16
104 | 260 | Single Battery Voltage_194 | 03 | 1 | mV | BMS | int16
105 | 261 | Single Battery Voltage_195 | 03 | 1 | mV | BMS | int16
106 | 262 | Single Battery Voltage_196 | 03 | 1 | mV | BMS | int16
107 | 263 | Single Battery Voltage_197 | 03 | 1 | mV | BMS | int16
108 | 264 | Single Battery Voltage_198 | 03 | 1 | mV | BMS | int16
109 | 265 | Single Battery Voltage_199 | 03 | 1 | mV | BMS | int16
10A | 266 | Single Battery Voltage_200 | 03 | 1 | mV | BMS | int16
10B | 267 | Single Battery Voltage_201 | 03 | 1 | mV | BMS | int16
10C | 268 | Single Battery Voltage_202 | 03 | 1 | mV | BMS | int16
10D | 269 | Single Battery Voltage_203 | 03 | 1 | mV | BMS | int16
10E | 270 | Single Battery Voltage_204 | 03 | 1 | mV | BMS | int16
10F | 271 | Single Battery Voltage_205 | 03 | 1 | mV | BMS | int16
110 | 272 | Single Battery Voltage_206 | 03 | 1 | mV | BMS | int16
111 | 273 | Single Battery Voltage_207 | 03 | 1 | mV | BMS | int16
112 | 274 | Single Battery Voltage_208 | 03 | 1 | mV | BMS | int16
113 | 275 | Single Battery Voltage_209 | 03 | 1 | mV | BMS | int16
114 | 276 | Single Battery Voltage_210 | 03 | 1 | mV | BMS | int16
115 | 277 | Single Battery Voltage_211 | 03 | 1 | mV | BMS | int16
116 | 278 | Single Battery Voltage_212 | 03 | 1 | mV | BMS | int16
117 | 279 | Single Battery Voltage_213 | 03 | 1 | mV | BMS | int16
118 | 280 | Single Battery Voltage_214 | 03 | 1 | mV | BMS | int16
119 | 281 | Single Battery Voltage_215 | 03 | 1 | mV | BMS | int16
11A | 282 | Single Battery Voltage_216 | 03 | 1 | mV | BMS | int16
11B | 283 | Single Battery Voltage_217 | 03 | 1 | mV | BMS | int16
11C | 284 | Single Battery Voltage_218 | 03 | 1 | mV | BMS | int16
11D | 285 | Single Battery Voltage_219 | 03 | 1 | mV | BMS | int16
11E | 286 | Single Battery Voltage_220 | 03 | 1 | mV | BMS | int16
11F | 287 | Single Battery Voltage_221 | 03 | 1 | mV | BMS | int16
120 | 288 | Single Battery Voltage_222 | 03 | 1 | mV | BMS | int16
121 | 289 | Single Battery Voltage_223 | 03 | 1 | mV | BMS | int16
122 | 290 | Single Battery Voltage_224 | 03 | 1 | mV | BMS | int16
123 | 291 | Single Battery Voltage_225 | 03 | 1 | mV | BMS | int16
124 | 292 | Single Battery Voltage_226 | 03 | 1 | mV | BMS | int16
125 | 293 | Single Battery Voltage_227 | 03 | 1 | mV | BMS | int16
126 | 294 | Single Battery Voltage_228 | 03 | 1 | mV | BMS | int16
127 | 295 | Single Battery Voltage_229 | 03 | 1 | mV | BMS | int16
128 | 296 | Single Battery Voltage_230 | 03 | 1 | mV | BMS | int16
129 | 297 | Single Battery Voltage_231 | 03 | 1 | mV | BMS | int16
12A | 298 | Single Battery Voltage_232 | 03 | 1 | mV | BMS | int16
12B | 299 | Single Battery Voltage_233 | 03 | 1 | mV | BMS | int16
12C | 300 | Single Battery Voltage_234 | 03 | 1 | mV | BMS | int16
12D | 301 | Single Battery Voltage_235 | 03 | 1 | mV | BMS | int16
12E | 302 | Single Battery Voltage_236 | 03 | 1 | mV | BMS | int16
12F | 303 | Single Battery Voltage_237 | 03 | 1 | mV | BMS | int16
130 | 304 | Single Battery Voltage_238 | 03 | 1 | mV | BMS | int16
131 | 305 | Single Battery Voltage_239 | 03 | 1 | mV | BMS | int16
132 | 306 | Single Battery Voltage_240 | 03 | 1 | mV | BMS | int16
133 | 307 | Single Battery Voltage_241 | 03 | 1 | mV | BMS | int16
134 | 308 | Single Battery Voltage_242 | 03 | 1 | mV | BMS | int16
135 | 309 | Single Battery Voltage_243 | 03 | 1 | mV | BMS | int16
136 | 310 | Single Battery Voltage_244 | 03 | 1 | mV | BMS | int16
137 | 311 | Single Battery Voltage_245 | 03 | 1 | mV | BMS | int16
138 | 312 | Single Battery Voltage_246 | 03 | 1 | mV | BMS | int16
139 | 313 | Single Battery Voltage_247 | 03 | 1 | mV | BMS | int16
13A | 314 | Single Battery Voltage_248 | 03 | 1 | mV | BMS | int16
13B | 315 | Single Battery Voltage_249 | 03 | 1 | mV | BMS | int16
13C | 316 | Single Battery Voltage_250 | 03 | 1 | mV | BMS | int16
13D | 317 | Single Battery Voltage_251 | 03 | 1 | mV | BMS | int16
13E | 318 | Single Battery Voltage_252 | 03 | 1 | mV | BMS | int16
13F | 319 | Single Battery Voltage_253 | 03 | 1 | mV | BMS | int16
140 | 320 | Single Battery Voltage_254 | 03 | 1 | mV | BMS | int16
141 | 321 | Single Battery Voltage_255 | 03 | 1 | mV | BMS | int16
142 | 322 | Single Battery Voltage_256 | 03 | 1 | mV | BMS | int16
143 | 323 | Single Battery Voltage_257 | 03 | 1 | mV | BMS | int16
144 | 324 | Single Battery Voltage_258 | 03 | 1 | mV | BMS | int16
145 | 325 | Single Battery Voltage_259 | 03 | 1 | mV | BMS | int16
146 | 326 | Single Battery Temperature_0 | 03 | 0.1 | ℃ | BMS | int16
147 | 327 | Single Battery Temperature_1 | 03 | 0.1 | ℃ | BMS | int16
148 | 328 | Single Battery Temperature_2 | 03 | 0.1 | ℃ | BMS | int16
149 | 329 | Single Battery Temperature_3 | 03 | 0.1 | ℃ | BMS | int16
14A | 330 | Single Battery Temperature_4 | 03 | 0.1 | ℃ | BMS | int16
14B | 331 | Single Battery Temperature_5 | 03 | 0.1 | ℃ | BMS | int16
14C | 332 | Single Battery Temperature_6 | 03 | 0.1 | ℃ | BMS | int16
14D | 333 | Single Battery Temperature_7 | 03 | 0.1 | ℃ | BMS | int16
14E | 334 | Single Battery Temperature_8 | 03 | 0.1 | ℃ | BMS | int16
14F | 335 | Single Battery Temperature_9 | 03 | 0.1 | ℃ | BMS | int16
150 | 336 | Single Battery Temperature_10 | 03 | 0.1 | ℃ | BMS | int16
151 | 337 | Single Battery Temperature_11 | 03 | 0.1 | ℃ | BMS | int16
152 | 338 | Single Battery Temperature_12 | 03 | 0.1 | ℃ | BMS | int16
153 | 339 | Single Battery Temperature_13 | 03 | 0.1 | ℃ | BMS | int16
154 | 340 | Single Battery Temperature_14 | 03 | 0.1 | ℃ | BMS | int16
155 | 341 | Single Battery Temperature_15 | 03 | 0.1 | ℃ | BMS | int16
156 | 342 | Single Battery Temperature_16 | 03 | 0.1 | ℃ | BMS | int16
157 | 343 | Single Battery Temperature_17 | 03 | 0.1 | ℃ | BMS | int16
158 | 344 | Single Battery Temperature_18 | 03 | 0.1 | ℃ | BMS | int16
159 | 345 | Single Battery Temperature_19 | 03 | 0.1 | ℃ | BMS | int16
15A | 346 | Single Battery Temperature_20 | 03 | 0.1 | ℃ | BMS | int16
15B | 347 | Single Battery Temperature_21 | 03 | 0.1 | ℃ | BMS | int16
15C | 348 | Single Battery Temperature_22 | 03 | 0.1 | ℃ | BMS | int16
15D | 349 | Single Battery Temperature_23 | 03 | 0.1 | ℃ | BMS | int16
15E | 350 | Single Battery Temperature_24 | 03 | 0.1 | ℃ | BMS | int16
15F | 351 | Single Battery Temperature_25 | 03 | 0.1 | ℃ | BMS | int16
160 | 352 | Single Battery Temperature_26 | 03 | 0.1 | ℃ | BMS | int16
161 | 353 | Single Battery Temperature_27 | 03 | 0.1 | ℃ | BMS | int16
162 | 354 | Single Battery Temperature_28 | 03 | 0.1 | ℃ | BMS | int16
163 | 355 | Single Battery Temperature_29 | 03 | 0.1 | ℃ | BMS | int16
164 | 356 | Single Battery Temperature_30 | 03 | 0.1 | ℃ | BMS | int16
165 | 357 | Single Battery Temperature_31 | 03 | 0.1 | ℃ | BMS | int16
166 | 358 | Single Battery Temperature_32 | 03 | 0.1 | ℃ | BMS | int16
167 | 359 | Single Battery Temperature_33 | 03 | 0.1 | ℃ | BMS | int16
168 | 360 | Single Battery Temperature_34 | 03 | 0.1 | ℃ | BMS | int16
169 | 361 | Single Battery Temperature_35 | 03 | 0.1 | ℃ | BMS | int16
16A | 362 | Single Battery Temperature_36 | 03 | 0.1 | ℃ | BMS | int16
16B | 363 | Single Battery Temperature_37 | 03 | 0.1 | ℃ | BMS | int16
16C | 364 | Single Battery Temperature_38 | 03 | 0.1 | ℃ | BMS | int16
16D | 365 | Single Battery Temperature_39 | 03 | 0.1 | ℃ | BMS | int16
16E | 366 | Single Battery Temperature_40 | 03 | 0.1 | ℃ | BMS | int16
16F | 367 | Single Battery Temperature_41 | 03 | 0.1 | ℃ | BMS | int16
170 | 368 | Single Battery Temperature_42 | 03 | 0.1 | ℃ | BMS | int16
171 | 369 | Single Battery Temperature_43 | 03 | 0.1 | ℃ | BMS | int16
172 | 370 | Single Battery Temperature_44 | 03 | 0.1 | ℃ | BMS | int16
173 | 371 | Single Battery Temperature_45 | 03 | 0.1 | ℃ | BMS | int16
174 | 372 | Single Battery Temperature_46 | 03 | 0.1 | ℃ | BMS | int16
175 | 373 | Single Battery Temperature_47 | 03 | 0.1 | ℃ | BMS | int16
176 | 374 | Single Battery Temperature_48 | 03 | 0.1 | ℃ | BMS | int16
177 | 375 | Single Battery Temperature_49 | 03 | 0.1 | ℃ | BMS | int16
178 | 376 | Single Battery Temperature_50 | 03 | 0.1 | ℃ | BMS | int16
179 | 377 | Single Battery Temperature_51 | 03 | 0.1 | ℃ | BMS | int16
17A | 378 | Single Battery Temperature_52 | 03 | 0.1 | ℃ | BMS | int16
17B | 379 | Single Battery Temperature_53 | 03 | 0.1 | ℃ | BMS | int16
17C | 380 | Single Battery Temperature_54 | 03 | 0.1 | ℃ | BMS | int16
17D | 381 | Single Battery Temperature_55 | 03 | 0.1 | ℃ | BMS | int16
17E | 382 | Single Battery Temperature_56 | 03 | 0.1 | ℃ | BMS | int16
17F | 383 | Single Battery Temperature_57 | 03 | 0.1 | ℃ | BMS | int16
180 | 384 | Single Battery Temperature_58 | 03 | 0.1 | ℃ | BMS | int16
181 | 385 | Single Battery Temperature_59 | 03 | 0.1 | ℃ | BMS | int16
182 | 386 | Single Battery Temperature_60 | 03 | 0.1 | ℃ | BMS | int16
183 | 387 | Single Battery Temperature_61 | 03 | 0.1 | ℃ | BMS | int16
184 | 388 | Single Battery Temperature_62 | 03 | 0.1 | ℃ | BMS | int16
185 | 389 | Single Battery Temperature_63 | 03 | 0.1 | ℃ | BMS | int16
186 | 390 | Single Battery Temperature_64 | 03 | 0.1 | ℃ | BMS | int16
187 | 391 | Single Battery Temperature_65 | 03 | 0.1 | ℃ | BMS | int16
188 | 392 | Single Battery Temperature_66 | 03 | 0.1 | ℃ | BMS | int16
189 | 393 | Single Battery Temperature_67 | 03 | 0.1 | ℃ | BMS | int16
18A | 394 | Single Battery Temperature_68 | 03 | 0.1 | ℃ | BMS | int16
18B | 395 | Single Battery Temperature_69 | 03 | 0.1 | ℃ | BMS | int16
18C | 396 | Single Battery Temperature_70 | 03 | 0.1 | ℃ | BMS | int16
18D | 397 | Single Battery Temperature_71 | 03 | 0.1 | ℃ | BMS | int16
18E | 398 | Single Battery Temperature_72 | 03 | 0.1 | ℃ | BMS | int16
18F | 399 | Single Battery Temperature_73 | 03 | 0.1 | ℃ | BMS | int16
190 | 400 | Single Battery Temperature_74 | 03 | 0.1 | ℃ | BMS | int16
191 | 401 | Single Battery Temperature_75 | 03 | 0.1 | ℃ | BMS | int16
192 | 402 | Single Battery Temperature_76 | 03 | 0.1 | ℃ | BMS | int16
193 | 403 | Single Battery Temperature_77 | 03 | 0.1 | ℃ | BMS | int16
194 | 404 | Single Battery Temperature_78 | 03 | 0.1 | ℃ | BMS | int16
195 | 405 | Single Battery Temperature_79 | 03 | 0.1 | ℃ | BMS | int16
196 | 406 | Single Battery Temperature_80 | 03 | 0.1 | ℃ | BMS | int16
197 | 407 | Single Battery Temperature_81 | 03 | 0.1 | ℃ | BMS | int16
198 | 408 | Single Battery Temperature_82 | 03 | 0.1 | ℃ | BMS | int16
199 | 409 | Single Battery Temperature_83 | 03 | 0.1 | ℃ | BMS | int16
19A | 410 | Single Battery Temperature_84 | 03 | 0.1 | ℃ | BMS | int16
19B | 411 | Single Battery Temperature_85 | 03 | 0.1 | ℃ | BMS | int16
19C | 412 | Single Battery Temperature_86 | 03 | 0.1 | ℃ | BMS | int16
19D | 413 | Single Battery Temperature_87 | 03 | 0.1 | ℃ | BMS | int16
19E | 414 | Single Battery Temperature_88 | 03 | 0.1 | ℃ | BMS | int16
19F | 415 | Single Battery Temperature_89 | 03 | 0.1 | ℃ | BMS | int16
1A0 | 416 | Single Battery Temperature_90 | 03 | 0.1 | ℃ | BMS | int16
1A1 | 417 | Single Battery Temperature_91 | 03 | 0.1 | ℃ | BMS | int16
1A2 | 418 | Single Battery Temperature_92 | 03 | 0.1 | ℃ | BMS | int16
1A3 | 419 | Single Battery Temperature_93 | 03 | 0.1 | ℃ | BMS | int16
1A4 | 420 | Single Battery Temperature_94 | 03 | 0.1 | ℃ | BMS | int16
1A5 | 421 | Single Battery Temperature_95 | 03 | 0.1 | ℃ | BMS | int16
1A6 | 422 | Single Battery Temperature_96 | 03 | 0.1 | ℃ | BMS | int16
1A7 | 423 | Single Battery Temperature_97 | 03 | 0.1 | ℃ | BMS | int16
1A8 | 424 | Single Battery Temperature_98 | 03 | 0.1 | ℃ | BMS | int16
1A9 | 425 | Single Battery Temperature_99 | 03 | 0.1 | ℃ | BMS | int16
1AA | 426 | Single Battery Temperature_100 | 03 | 0.1 | ℃ | BMS | int16
1AB | 427 | Single Battery Temperature_101 | 03 | 0.1 | ℃ | BMS | int16
1AC | 428 | Single Battery Temperature_102 | 03 | 0.1 | ℃ | BMS | int16
1AD | 429 | Single Battery Temperature_103 | 03 | 0.1 | ℃ | BMS | int16
1AE | 430 | Single Battery Temperature_104 | 03 | 0.1 | ℃ | BMS | int16
1AF | 431 | Single Battery Temperature_105 | 03 | 0.1 | ℃ | BMS | int16
1B0 | 432 | Single Battery Temperature_106 | 03 | 0.1 | ℃ | BMS | int16
1B1 | 433 | Single Battery Temperature_107 | 03 | 0.1 | ℃ | BMS | int16
1B2 | 434 | Single Battery Temperature_108 | 03 | 0.1 | ℃ | BMS | int16
1B3 | 435 | Single Battery Temperature_109 | 03 | 0.1 | ℃ | BMS | int16
1B4 | 436 | Single Battery Temperature_110 | 03 | 0.1 | ℃ | BMS | int16
1B5 | 437 | Single Battery Temperature_111 | 03 | 0.1 | ℃ | BMS | int16
1B6 | 438 | Single Battery Temperature_112 | 03 | 0.1 | ℃ | BMS | int16
1B7 | 439 | Single Battery Temperature_113 | 03 | 0.1 | ℃ | BMS | int16
1B8 | 440 | Single Battery Temperature_114 | 03 | 0.1 | ℃ | BMS | int16
1B9 | 441 | Single Battery Temperature_115 | 03 | 0.1 | ℃ | BMS | int16
1BA | 442 | Single Battery Temperature_116 | 03 | 0.1 | ℃ | BMS | int16
1BB | 443 | Single Battery Temperature_117 | 03 | 0.1 | ℃ | BMS | int16
1BC | 444 | Single Battery Temperature_118 | 03 | 0.1 | ℃ | BMS | int16
1BD | 445 | Single Battery Temperature_119 | 03 | 0.1 | ℃ | BMS | int16
1BE | 446 | Single Battery Temperature_120 | 03 | 0.1 | ℃ | BMS | int16
1BF | 447 | Single Battery Temperature_121 | 03 | 0.1 | ℃ | BMS | int16
1C0 | 448 | Single Battery Temperature_122 | 03 | 0.1 | ℃ | BMS | int16
1C1 | 449 | Single Battery Temperature_123 | 03 | 0.1 | ℃ | BMS | int16
1C2 | 450 | Single Battery Temperature_124 | 03 | 0.1 | ℃ | BMS | int16
1C3 | 451 | Single Battery Temperature_125 | 03 | 0.1 | ℃ | BMS | int16
1C4 | 452 | Single Battery Temperature_126 | 03 | 0.1 | ℃ | BMS | int16
1C5 | 453 | Single Battery Temperature_127 | 03 | 0.1 | ℃ | BMS | int16
1C6 | 454 | Single Battery Temperature_128 | 03 | 0.1 | ℃ | BMS | int16
1C7 | 455 | Single Battery Temperature_129 | 03 | 0.1 | ℃ | BMS | int16
1C8 | 456 | Single Battery Temperature_130 | 03 | 0.1 | ℃ | BMS | int16
1C9 | 457 | Single Battery Temperature_131 | 03 | 0.1 | ℃ | BMS | int16
1CA | 458 | Single Battery Temperature_132 | 03 | 0.1 | ℃ | BMS | int16
1CB | 459 | Single Battery Temperature_133 | 03 | 0.1 | ℃ | BMS | int16
1CC | 460 | Single Battery Temperature_134 | 03 | 0.1 | ℃ | BMS | int16
1E6 | 486 | Operational status | 03 | 1 |  | TMS | uint16 | 1- Cooling Mode 2- Heating Mode 3- Recirculation Mode 0- Power Off
1E7 | 487 | utlet Water Temperature | 03 | 0.1 | ℃ | TMS | uint16
1E8 | 488 | Return Water Temperature | 03 | 0.1 | ℃ | TMS | uint16
1E9 | 489 | Ambient Temperature | 03 | 0.1 | ℃ | TMS | uint16
1EA | 490 | Inlet Pressure Value | 03 | 0.1 | Bar | TMS | uint16
1EB | 491 | Outlet Pressure Value | 03 | 0.1 | Bar | TMS | uint16
1EC | 492 | TMS Fault Code | 03 | 1 |  | TMS | int16 | Fault code: Specific fault explanationsare reflected in registers 700-726. A non-zero value indicates a fault
1ED | 493 | Voltage | 03 | 1 | V | TMS | int16
1EE | 494 | High Pressure Value | 03 | 1 | Kpa | TMS | int16
1EF | 495 | Low Pressure Value | 03 | 1 | Kpa | TMS | int16
1F0 | 496 | Fan PWM | 03 | 1 | % | TMS | int16
1F1 | 497 | Compressor Speed | 03 | 1 | rpm | TMS | int16
1F2 | 498 | Compressor Current | 03 | 0.1 | A | TMS | int16
1F3 | 499 | Compressor Power | 03 | 0.1 | kW | TMS | int16
1F4 | 500 | Active Power | 03 | 0.1 | kW | METER | int16
1F5 | 501 | Total Forward Active Energy | 03 | 0.1 | kWh | METER | uint16
1F6 | 502 | Total Reverse Active Energy | 03 | 0.1 | kWh | METER | uint16
1F7 | 503 | Total Current | 03 | 0.1 | A | METERJ | int16
1F8 | 504 | Phase A Current | 03 | 0.1 | A | METERJ | int16
1F9 | 505 | Phase B Current | 03 | 0.1 | A | METERJ | int16
1FA | 506 | Phase C Current | 03 | 0.1 | A | METERJ | int16
1FB | 507 | Phase A Voltage | 03 | 0.1 | V | METERJ | int16
1FC | 508 | Phase B Voltage | 03 | 0.1 | V | METERJ | int16
1FD | 509 | Phase C Voltage | 03 | 0.1 | V | METERJ | int16
1FE | 510 | Frequency | 03 | 0.1 | Hz | METERJ | int16
1FF | 511 | Total Active Power | 03 | 0.1 | Kw | METERJ | int16
200 | 512 | Total Reactive Power | 03 | 0.1 | kVar | METERJ | int16
201 | 513 | Total Power Factor | 03 | 0.1 |  | METERJ | int16
202 | 514 | Total Forward Active Energy | 03 | 0.1 | kWh | METERJ | uint16
203 | 515 | Total Reverse Active Energy | 03 | 0.1 | kWh | METERJ | uint16
332 | 818 | System alarms | 03 | 1 |  | SYS | uint16 | Bit0：Water Leakage Bit1：Access Control Bit2：BMS Fault Bit3：BMS Alarm Bit4：PCS Communication Abnormality Bit5：BMS Communication Abnormality Bit6：Cooling Communication Abnormality Bit7：Remote Communication Fault Bit8-Bit15：Spare
333 | 819 | System failure | 03 | 1 |  | SYS | uint16 | Bit0：Cabin Fire Fault Bit1：PCS Fault Bit2：Batt Fire Fault Bit3-Bit15：Spare
334 | 820 | System protect | 03 | 1 |  | SYS | uint16 | Bit0-Bit2：Spare Bit3：SOC Over Limit Bit4-Bit11：Spare Bit12：Cell Temperature Protection Bit13：Cell Under Vol Bit14：Cell Over Vol Bit15：Spare
33C | 828 | Single overvoltage limiting voltage | 03 | 0.01 | V | SYS | int16
33D | 829 | Single-cell Undervoltage Limit Voltage | 03 | 0.01 | V | SYS | int16
33E | 830 | Single-cell Overtemperature Limit Temperature | 03 | 0.1 | ℃ | SYS | int16
33F | 831 | Single-cell Undertemperature Limit Temperature | 03 | 0.1 | ℃ | SYS | int16
340 | 832 | BMS Heating Setpoint | 03 | 0.1 | ℃ | SYS | int16
341 | 833 | BMS Heating Hysteresis | 03 | 0.1 | ℃ | SYS | int16
342 | 834 | BMS Heating Target Temperature | 03 | 0.1 | ℃ | SYS | int16
343 | 835 | BMS Cooling Setpoint | 03 | 0.1 | ℃ | SYS | int16
344 | 836 | BMS Cooling Hysteresis | 03 | 0.1 | ℃ | SYS | int16
345 | 837 | BMS Cooling Target Temperature | 03 | 0.1 | ℃ | SYS | int16
346 | 838 | PCS Cooling Setpoint | 03 | 0.1 | ℃ | SYS | int16
347 | 839 | PCS Cooling Hysteresis | 03 | 0.1 | ℃ | SYS | int16
348 | 840 | PCS Cooling Target Temperature | 03 | 0.1 | ℃ | SYS | int16
349 | 841 | Single-cell Overvoltage Level 3 Alarm Threshold | 03 | 1 | mV | BMS | u16
34A | 842 | Single-cell Overvoltage Level 3 Recovery Threshold | 03 | 1 | mV | BMS | u16
34B | 843 | Single-cell Undervoltage Level 3 Alarm Threshold | 03 | 1 | mV | BMS | u16
34C | 844 | Single-cell Undervoltage Level 3 Recovery Threshold | 03 | 1 | mV | BMS | u16
34D | 845 | Total Voltage Overvoltage Level 3 Alarm Threshold | 03 | 0.1 | V | BMS | u16
34E | 846 | Total Voltage Overvoltage Level 3 Recovery Threshold | 03 | 0.1 | V | BMS | u16
34F | 847 | Total Voltage Undervoltage Level 3 Alarm Threshold | 03 | 0.1 | V | BMS | u16
350 | 848 | Total Voltage Undervoltage Level 3 Recovery Threshold | 03 | 0.1 | V | BMS | u16
351 | 849 | Charging Overcurrent Level 3 Alarm Threshold | 03 | 0.1 | A | BMS | u16
352 | 850 | Charging Overcurrent Level 3 Recovery Threshold | 03 | 0.1 | A | BMS | u16
353 | 851 | Discharging Overcurrent Level 3 Alarm Threshold | 03 | 0.1 | A | BMS | u16
354 | 852 | Discharging Overcurrent Level 3 Recovery Threshold | 03 | 0.1 | A | BMS | u16
355 | 853 | Charging Temperature Overhigh Level 3 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
356 | 854 | Charging Temperature Overhigh Level 3 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
357 | 855 | Charging Temperature Overlow Level 3 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
358 | 856 | Charging Temperature Overlow Level 3 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
359 | 857 | SOC Overlow Level 3 Alarm Threshold | 03 | 1 | % | BMS | u16
35A | 858 | SOC Overlow Level 3 Recovery Threshold | 03 | 1 | % | BMS | u16
35B | 859 | Terminal Temperature Overhigh Level 3 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
35C | 860 | Terminal Temperature Overhigh Level 3 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
35D | 861 | Insulation Failure Level 3 Alarm Threshold | 03 | 1 | Ω/V | BMS | u16
35E | 862 | Insulation Failure Level 3 Recovery Threshold | 03 | 1 | Ω/V | BMS | u16
35F | 863 | Single-cell Voltage Difference Overhigh Level 3 Alarm Threshold | 03 | 1 | mV | BMS | u16
360 | 864 | Single-cell Voltage Difference Overhigh Level 3 Recovery Threshold | 03 | 1 | mV | BMS | u16
361 | 865 | Total Voltage Difference Overhigh Level 3 Alarm Threshold | 03 | 0.1 | V | BMS | u16
362 | 866 | Total Voltage Difference Overhigh Level 3 Recovery Threshold | 03 | 0.1 | V | BMS | u16
363 | 867 | Discharging Overtemperature Level 3 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
364 | 868 | Discharging Overtemperature Level 3 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
365 | 869 | Discharging Undertemperature Level 3 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
366 | 870 | Discharging Undertemperature Level 3 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
367 | 871 | Temperature Difference Overhigh Level 3 Alarm Threshold | 03 | 0.1 | ℃ | BMS | u16
368 | 872 | Temperature Difference Overhigh Level 3 Recovery Threshold | 03 | 0.1 | ℃ | BMS | u16
369 | 873 | High-voltage Box Overtemperature Level 3 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
36A | 874 | High-voltage Box Overtemperature Level 3 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
36B | 875 | Single-cell Overvoltage Level 2 Alarm Threshold | 03 | 1 | mV | BMS | u16
36C | 876 | Single-cell Overvoltage Level 2 Recovery Threshold | 03 | 1 | mV | BMS | u16
36D | 877 | Single-cell Undervoltage Level 2 Alarm Threshold | 03 | 1 | mV | BMS | u16
36E | 878 | Single-cell Undervoltage Level 2 Recovery Threshold | 03 | 1 | mV | BMS | u16
36F | 879 | Total Voltage Overvoltage Level 2 Alarm Threshold | 03 | 0.1 | V | BMS | u16
370 | 880 | Total Voltage Overvoltage Level 2 Recovery Threshold | 03 | 0.1 | V | BMS | u16
371 | 881 | Total Voltage Undervoltage Level 2 Alarm Threshold | 03 | 0.1 | V | BMS | u16
372 | 882 | Total Voltage Undervoltage Level 2 Recovery Threshold | 03 | 0.1 | V | BMS | u16
373 | 883 | Charging Overcurrent Level 2 Alarm Threshold | 03 | 0.1 | A | BMS | u16
374 | 884 | Charging Overcurrent Level 2 Recovery Threshold | 03 | 0.1 | A | BMS | u16
375 | 885 | Discharging Overcurrent Level 2 Alarm Threshold | 03 | 0.1 | A | BMS | u16
376 | 886 | Discharging Overcurrent Level 2 Recovery Threshold | 03 | 0.1 | A | BMS | u16
377 | 887 | Charging Temperature Overhigh Level 2 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
378 | 888 | Charging Temperature Overhigh Level 2 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
379 | 889 | Charging Temperature Overlow Level 2 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
37A | 890 | Charging Temperature Overlow Level 2 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
37B | 891 | SOC Overlow Level 2 Alarm Threshold | 03 | 1 | % | BMS | u16
37C | 892 | SOC Overlow Level 2 Recovery Threshold | 03 | 1 | % | BMS | u16
37D | 893 | Terminal Temperature Overhigh Level 2 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
37E | 894 | Terminal Temperature Overhigh Level 2 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
37F | 895 | Insulation Failure Level 2 Alarm Threshold | 03 | 1 | Ω/V | BMS | u16
380 | 896 | Insulation Failure Level 2 Recovery Threshold | 03 | 1 | Ω/V | BMS | u16
381 | 897 | Single-cell Voltage Difference Overhigh Level 2 Alarm Threshold | 03 | 1 | mV | BMS | u16
382 | 898 | Single-cell Voltage Difference Overhigh Level 2 Recovery Threshold | 03 | 1 | mV | BMS | u16
383 | 899 | Total Voltage Difference Overhigh Level 2 Alarm Threshold | 03 | 0.1 | V | BMS | u16
384 | 900 | Total Voltage Difference Overhigh Level 2 Recovery Threshold | 03 | 0.1 | V | BMS | u16
385 | 901 | Discharging Overtemperature Level 2 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
386 | 902 | Discharging Overtemperature Level 2 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
387 | 903 | Discharging Undertemperature Level 2 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
388 | 904 | Discharging Undertemperature Level 2 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
389 | 905 | Temperature Difference Overhigh Level 2 Alarm Threshold | 03 | 0.1 | ℃ | BMS | u16
38A | 906 | Temperature Difference Overhigh Level 2 Recovery Threshold | 03 | 0.1 | ℃ | BMS | u16
38B | 907 | High-voltage Box Overtemperature Level 2 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
38C | 908 | High-voltage Box Overtemperature Level 2 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
38D | 909 | Single-cell Overvoltage Level 1 Alarm Threshold | 03 | 1 | mV | BMS | u16
38E | 910 | Single-cell Overvoltage Level 1 Recovery Threshold | 03 | 1 | mV | BMS | u16
38F | 911 | Single-cell Undervoltage Level 1 Alarm Threshold | 03 | 1 | mV | BMS | u16
390 | 912 | Single-cell Undervoltage Level 1 Recovery Threshold | 03 | 1 | mV | BMS | u16
391 | 913 | Total Voltage Overvoltage Level 1 Alarm Threshold | 03 | 0.1 | V | BMS | u16
392 | 914 | Total Voltage Overvoltage Level 1 Recovery Threshold | 03 | 0.1 | V | BMS | u16
393 | 915 | Total Voltage Undervoltage Level 1 Alarm Threshold | 03 | 0.1 | V | BMS | u16
394 | 916 | Total Voltage Undervoltage Level 1 Recovery Threshold | 03 | 0.1 | V | BMS | u16
395 | 917 | Charging Overcurrent Level 1 Alarm Threshold | 03 | 0.1 | A | BMS | u16
396 | 918 | Charging Overcurrent Level 1 Recovery Threshold | 03 | 0.1 | A | BMS | u16
397 | 919 | Discharging Overcurrent Level 1 Alarm Threshold | 03 | 0.1 | A | BMS | u16
398 | 920 | Discharging Overcurrent Level 1 Recovery Threshold | 03 | 0.1 | A | BMS | u16
399 | 921 | Charging Temperature Overhigh Level 1 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
39A | 922 | Charging Temperature Overhigh Level 1 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
39B | 923 | Charging Temperature Overlow Level 1 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
39C | 924 | Charging Temperature Overlow Level 1 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
39D | 925 | SOC Overlow Level 1 Alarm Threshold | 03 | 1 | % | BMS | u16
39E | 926 | SOC Overlow Level 1 Recovery Threshold | 03 | 1 | % | BMS | u16
39F | 927 | Terminal Temperature Overhigh Level 1 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
3A0 | 928 | Terminal Temperature Overhigh Level 1 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
3A1 | 929 | Insulation Failure Level 1 Alarm Threshold | 03 | 1 | Ω/V | BMS | u16
3A2 | 930 | Insulation Failure Level 1 Recovery Threshold | 03 | 1 | Ω/V | BMS | u16
3A3 | 931 | Single-cell Voltage Difference Overhigh Level 1 Alarm Threshold | 03 | 1 | mV | BMS | u16
3A4 | 932 | Single-cell Voltage Difference Overhigh Level 1 Recovery Threshold | 03 | 1 | mV | BMS | int16
3A5 | 933 | Total Voltage Difference Overhigh Level 1 Alarm Threshold | 03 | 0.1 | V | BMS | u16
3A6 | 934 | Total Voltage Difference Overhigh Level 1 Recovery Threshold | 03 | 0.1 | V | BMS | u16
3A7 | 935 | Discharging Overtemperature Level 1 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
3A8 | 936 | Discharging Overtemperature Level 1 Recovery Threshold | 03 | 0.1 | ℃ | BMS | u16
3A9 | 937 | Discharging Undertemperature Level 1 Alarm Threshold | 03 | 0.1 | ℃ | BMS | u16
3AA | 938 | Discharging Undertemperature Level 1 Recovery Threshold | 03 | 0.1 | ℃ | BMS | u16
3AB | 939 | Temperature Difference Overhigh Level 1 Alarm Threshold | 03 | 0.1 | ℃ | BMS | u16
3AC | 940 | Temperature Difference Overhigh Level 1 Recovery Threshold | 03 | 0.1 | ℃ | BMS | u16
3AD | 941 | High-voltage Box Overtemperature Level 1 Alarm Threshold | 03 | 0.1 | ℃ | BMS | int16
3AE | 942 | High-voltage Box Overtemperature Level 1 Recovery Threshold | 03 | 0.1 | ℃ | BMS | int16
3BE | 958 | STScode | 03 | 1 |  | PCS | u16
3BF | 959 | chargelimit | 03 | 1 | kW | SYS | int16
3C0 | 960 | dischargelimit | 03 | 1 | kW | SYS | int16

## remote operation&control
Hex Address | Decimal Address | Signal Name | FunctionCode | Type
2D7 | 727 | System Startup | 03/06/10 | int16 | 1-Power On
2D8 | 728 | System Shutdown | 03/06/10 | int16 | 1-Power Off
2D9 | 729 | System Reset | 06/10 | int16 | 1-Reset
2DA | 730 | Active Power Set | 03/06/10 | int16 | ratio:0.1,for example 505=50.5，Negative charging and positive discharging
2DB | 731 | Reverse Power Protection | 03/06/10 | int16 | Simultaneous Dispatch Required: Reverse Power Protection: 1-Enable 0-Disable
2DC | 732 | Reverse Power Threshold | 03/06/10 | int16
2DD | 733 | Maximum Demand Protection | 03/06/10 | int16 | Simultaneous Dispatch Required Demand Protection: 1-Enable 0-Disable
2DE | 734 | Maximum Demand Protection Value | 03/06/10 | int16
2E2 | 738 | Group Control | 03/06/10 | int16 | Simultaneous Dispatch Required: Group Control: 1-Enable 0-Disable. 1-Master 0-Slave
2E3 | 739 | Group ID | 03/06/10 | int16
2E4 | 740 | Master/Slave | 03/06/10 | int16
2E5 | 741 | PCS Mode Switch | 03/06/10 | uint16 | 0-Shutdown Mode 1-DC Constant Current 2-DC Constant Voltage 3-DC Constant Power 4-AC Constant Power 5-AC Constant Voltage 6-DC Source 7-VSG Mode
2E6 | 742 | PCS Reactive Model Switch | 03/06/10 | uint16 | 0 - Disabled 1 - Power Factor Control Mode 2 - Reactive Power Control Mode
2E7 | 743 | Reactive Power Set | 03/06/10 | int16 | ratio:0.1,for example 505=50.5 Effective only in Reactive Power Control Mode
2E8 | 744 | Power Factor Set | 03/06/10 | uint16 | Effective only in Power Factor Control Mode
2E9 | 745 | Off-grid voltage settings | 03/06/10 | uint16 | The voltage range is 300V-440V
2EA | 746 | Off-grid frequency settings | 03/06/10 | uint16 | Frequency range 45Hz-55Hz，ratio:0.1
2EB | 747 | In-place/remote setup | 03/06/10 | int16 | 0 - Locality 1 - Remote, Localism Mode cannot remotely control the program
2EC | 748 | Grid code | 03/06 | int16 | Bits 0-11: Grid Code 0: China 1: United Kingdom 2: European Union (EU) 3: Germany 4: Austria 5: Poland Bits 12-15: Grid Subcode (0~15, representing different standards under the same country): When Grid Code = 3 (Germany): Subcode 0: 4105 Standard Subcode 1: 4110 Standard Subcode 2: 4120 Standard. When Grid Code = 4 (Austria): Subcode 0: TORA Standard Subcode 1: TORB Standard.
2ED | 749 | Time Constant | 03/06/10 | int16 | ratio:1
2EE | 750 | Damping Coef | 03/06/10 | int16 | ratio:1
2EF | 751 | Freq. Coef. | 03/06/10 | int16 | ratio:1
2F0 | 752 | Volt. Coef. | 03/06/10 | int16 | ratio:1
2F1 | 753 | STS bypass mode | 03/06/10 | uint16 | ratio:1 0 - STS bypass mode is not enabled 1- Enable STS bypass working mode
2F2 | 754 | Mode Switch | 06/10 | int16 | bit0-bit6 represent Monday to Sunday respectively. Simultaneous Dispatch Required 1-Manual Mode 2-Scheduled Mode. "The start time (or end time) needs to be converted into the number of minutes elapsed since 00:00. For example, 02:00 would be converted to 120 minutes." The scheduled mode requires a full time arrangement from 00:00 to 23:59, with periods that do not require charging or discharging set to standby mode.
2F3 | 755 | Weekday Value | 06/10 | int16
2F4 | 756 | Start Time | 06/10 | int16
2F5 | 757 | End Time | 06/10 | int16
2F6 | 758 | Value | 06/10 | int16
2F7 | 759 | Start Time2 （Last End Time） | 06/10
2F8 | 760 | End Time2 | 06/10
2F9 | 761 | Value2 | 06/10
2FA | 762 | Start Time3（Last End Time2） | 06/10
2FB | 763 | End Time3 | 06/10
2FC | 764 | Value3 | 06/10
... |  | Start Time..（Last End Time..） | 06/10
… |  | End Time.. | 06/10
… |  | Value.. | 06/10
335 | 821 | year | 03/06/10 | int16
336 | 822 | month | 03/06/10 | int16
337 | 823 | day | 03/06/10 | int16
338 | 824 | time | 03/06/10 | int16
339 | 825 | minute | 03/06/10 | int16
33A | 826 | second | 03/06/10 | int16
33B | 827 | time zone | 03/06/10 | int16

## alarm
source | Decimal Address
PCS | 28 | Total Fault Points of PCS
PCS | 555-629 | PCS specific fault explanation
BMS | 61,62,63,64,65 | 61 Corresponding to BMS 3-level alarm 62 Corresponding to BMS 2-level alarm 63 Corresponding to BMS 1-level alarm 64 Corresponding to the total failure of the BMS 65 Corresponding to the BMS total alarm
BMS | 630-693 | 630-677 Contains a specific explanation of BMS123 level alarms 678-686 Contains a specific explanation of the BMS failure 687-693 Contains a specific explanation of the fire signal alarm accepted by the BMS
TMS | 694-726 | Contains all TMS fault information
SYS | 552-554,818-820 | 552 Door Status 553 Water Immersion 554 Fire Protection 818 Contains the specific information of the system alarm 819 Contains the specific information of the system failures 820 Contains the specific information of the system project