## CIF Price Targets
BESS CIF PRICE TARGETS — Lighthief Cyprus Ltd
Confidential ¦ Prepared: 06 March 2026 ¦ All prices CIF Limassol (EUR) ¦ Incoterms: CIF
2-Hour Duration Systems (C-rate = 0.5C)
Power (MW) | Energy (MWh) | Duration (h) | Containers (est.) | Reference CIF €/kWh | Target CIF €/kWh | Reference CIF Total | Target CIF Total | Notes
1 | 2 | 2 | 1 | 125 | 115 | 250000 | 230000 | Small system premium
2.5 | 5 | 2 | 1 | 118 | 108 | 590000 | 540000
5 | 10 | 2 | 2 | 110.11 | 100 | 1101100 | 1000000 | Based on 5MW/10MWh actual
10 | 20 | 2 | 4 | 100 | 92 | 2000000 | 1840000
25 | 50 | 2 | 10 | 92 | 84 | 4600000 | 4200000 | Volume pricing target
50 | 100 | 2 | 20 | 88 | 80 | 8800000 | 8000000 | Large-scale benchmark
4-Hour Duration Systems (C-rate = 0.25C)
Power (MW) | Energy (MWh) | Duration (h) | Containers (est.) | Reference CIF €/kWh | Target CIF €/kWh | Reference CIF Total | Target CIF Total | Notes
1 | 4 | 4 | 1 | 121.87 | 112 | 487480 | 448000 | Based on 1MW/4MWh actual (€509,420)
2.5 | 10 | 4 | 2 | 97.14 | 90 | 971400 | 900000 | Based on 2.5MW/10MWh actual (€974,457)
5 | 20 | 4 | 4 | 92.14 | 85 | 1842800 | 1700000 | Based on 5MW/20MWh actual (€1,848,712)
10 | 40 | 4 | 8 | 94.25 | 86 | 3770000 | 3440000 | Based on 12MW/40MWh actual (€3,781,992)
25 | 100 | 4 | 20 | 87.54 | 80 | 8754000 | 8000000 | Based on 25MW/100MWh actual (€8,782,302)
50 | 200 | 4 | 40 | 84 | 76 | 16800000 | 15200000 | Extrapolated volume target
8-Hour Duration Systems (C-rate = 0.125C)
Power (MW) | Energy (MWh) | Duration (h) | Containers (est.) | Reference CIF €/kWh | Target CIF €/kWh | Reference CIF Total | Target CIF Total | Notes
1 | 8 | 8 | 2 | 108 | 98 | 864000 | 784000 | Estimated from portfolio curve
2.5 | 20 | 8 | 4 | 94 | 86 | 1880000 | 1720000
5 | 40 | 8 | 8 | 88 | 80 | 3520000 | 3200000
8 | 60 | 8 | 12 | 82.03 | 76 | 4921800 | 4560000 | Based on 8MW/60MWh actual (€4,937,363)
10 | 80 | 8 | 16 | 80 | 74 | 6400000 | 5920000 | Volume target
25 | 200 | 8 | 40 | 78 | 72 | 15600000 | 14400000 | Large-scale 8h target
50 | 400 | 8 | 80 | 76 | 70 | 30400000 | 28000000 | Benchmark competitive pricing
Reference CIF = Current portfolio pricing (887 MWh across 51 parks, Q1 2026). Target CIF = Competitive pricing expectation for new supplier.
All prices EUR, CIF Limassol. CIF scope: BESS containers (EVE LFP cells) + Grid-Forming PCS (Kehua C-HUD series or equivalent) + MV Transformer/Skid + MV Switchgear + BMS + Fire Suppression + Liquid Cooling + Commissioning.
Container count is approximate based on ~5 MWh per 20ft HC container. Actual count depends on supplier container capacity.

## Actual CIF Data
ACTUAL CIF PRICING — Current Portfolio (Q1 2026)
Portfolio: 51 parks, 249 MW, 887 MWh ¦ Total CIF: €85,963,925 ¦ EVE LFP cells, Kehua C-HUD Grid-Forming PCS ¦ CIF Limassol
CIF by System Configuration (sorted by €/kWh ascending)
Configuration | Power (MW) | Energy (MWh) | Duration (h) | CIF Total (€) | CIF €/kWh | # in Portfolio | Containers
8MW / 60MWh | 8 | 60 | 7.5 | 4937363 | 82.03 | 1 | 14
25MW / 100MWh | 25 | 100 | 4 | 8782302 | 87.54 | 1 | 22
7MW / 30MWh | 7 | 30 | 4.29 | 2731668 | 90.77 | 1 | 10
5MW / 20MWh | 5 | 20 | 4 | 1848712 | 92.14 | 2 | 5
8MW / 35MWh | 8 | 35 | 4.38 | 3303521 | 94.09 | 1 | 9
12MW / 40MWh | 12 | 40 | 3.33 | 3781992 | 94.25 | 5 | 12
6MW / 20MWh | 6 | 20 | 3.33 | 1907319 | 95.06 | 1 | 6
6.5MW / 20MWh | 6.5 | 20 | 3.08 | 1951711 | 97.27 | 1 | 5
2.5MW / 10MWh | 2.5 | 10 | 4 | 974457 | 97.14 | 2 | 3
7.5MW / 25MWh | 7.5 | 25 | 3.33 | 2476650 | 98.75 | 1 | 7
3MW / 10MWh | 3 | 10 | 3.33 | 993203 | 99 | 3 | 3
5MW / 15MWh | 5 | 15 | 3 | 1592099 | 99 | 4 | 5
7MW / 20MWh | 7 | 20 | 2.86 | 2001737 | 99.77 | 1 | 6
7.7MW / 25MWh | 7.7 | 25 | 3.25 | 2523653 | 100.62 | 2 | 7
3.29MW / 10MWh | 3.29 | 10 | 3.04 | 1007809 | 100.46 | 1 | 3
4MW / 15MWh | 4 | 15 | 3.75 | 1562533 | 103.84 | 2 | 4
4.5MW / 15MWh | 4.5 | 15 | 3.33 | 1562533 | 103.84 | 1 | 4
2.5MW / 7.5MWh | 2.5 | 7.5 | 3 | 871308 | 104.22 | 3 | 3
5MW / 10MWh | 5 | 10 | 2 | 1104571 | 110.11 | 3 | 3
3.5MW / 10MWh | 3.5 | 10 | 2.86 | 1064650 | 106.13 | 1 | 3
3MW / 12MWh | 3 | 12 | 4 | 1347385 | 107.45 | 1 | 4
1MW / 5MWh | 1 | 5 | 5 | 560994 | 111.84 | 1 | 2
1.5MW / 5MWh | 1.5 | 5 | 3.33 | 585977 | 116.82 | 4 | 2
2MW / 5MWh | 2 | 5 | 2.5 | 602846 | 120.19 | 1 | 2
1MW / 4MWh | 1 | 4 | 4 | 509420 | 121.87 | 2 | 2
1.5MW / 5MWh (Paphos) | 1.5 | 5 | 3.33 | 541047 | 129.44 | 1 | 2
Portfolio CIF Summary
Total Portfolio CIF | €85,963,925
Total Capacity | 887 MWh (249 MW)
Weighted Average CIF | €96.94/kWh (€96,940/MWh)
CIF Range | €82.03 - €129.44/kWh
Total Parks | 51 (46 active + 5 future)
Cell Supplier | EVE Energy (LFP, 314Ah, Tier-1)
PCS | Kehua C-HUD Series (Grid-Forming Capable)
Incoterms | CIF Limassol

## CIF Scope & Requirements
CIF SCOPE DEFINITION — What Must Be Included in CIF Price
This defines the minimum scope that all CIF quotations must cover to be comparable.
INCLUDED in CIF Price (Mandatory)
Component | Description | Specification | Status
BESS Containers | LFP battery containers, fully integrated | ~5 MWh per 20ft HC container | Required
LFP Battery Cells | Tier-1 LFP cells (EVE 314Ah or equivalent) | EVE Energy, CATL, BYD, or CALB — must be BNEF Tier-1 | Required
Battery Management System | Container-level BMS | Cell/module/rack/container levels, IEC 62619 | Required
Grid-Forming PCS | Bi-directional inverter, grid-forming capable | Kehua BCS1000K-C-HUD / BCS1250K-C-HUD or equivalent, ≥98% eff. | Required
MV Transformer | Step-up transformer (MV Skid) | Oil-immersed or dry-type, matched to grid voltage | Required
MV Switchgear | Ring Main Unit / switchgear | 22kV rated, Schneider/ABB or equivalent | Required
Fire Suppression | In-container fire suppression | Aerosol + gas detection + early warning | Required
Liquid Cooling System | Active thermal management | 45kW cooling capacity per container | Required
C5 Corrosion Coating | Marine/coastal corrosion protection | ISO 12944-5 C5-M standard | Required
Communication Protocols | SCADA/EMS integration ready | Modbus TCP, IEC 60870-5-104, IEC 61850 | Required
Training & Commissioning | On-site commissioning support | Factory training + site commissioning crew | Required
Shipping | CIF to destination port | CIF Limassol, marine cargo insurance included | Required
5-Year Base Warranty | Standard defect/performance warranty | 5 years excl. consumables | Required
Grid Code Certification | EU grid code compliance | EN 50549-2 (or TÜV equivalent) | Required
EXCLUDED from CIF (EPC Scope — Provided Separately)
Item | Description | Typical Cost | Responsibility
DC Cabling | Inter-container DC connections | Varies by layout | EPC / Lighthief
AC Cabling (LV) | LV cabling from PCS to transformer | ~€1,400/MW | EPC / Lighthief
MV Cabling | MV cables from transformer to grid PCC | ~€3,500/feeder | EPC / Lighthief
Civil Works | Concrete pads, foundations, fencing | ~€2,000/MWh | EPC / Lighthief
Earthworks & Drainage | Site preparation and drainage | Included in civil works | EPC / Lighthief
EMS / SCADA | Energy Management System | Quoted separately | EPC / Lighthief
Lightning Protection | External LPS and SPDs | Quoted separately | Client / EPC
Import Duties | Cyprus customs (weighted ~2.66%) | 2.66% of CIF | EPC / Lighthief
Inland Transport | Port to site delivery | ~€2,360/container | EPC / Lighthief
Key Technical Requirements
Parameter | Minimum Requirement | Preferred | Notes
Cell Chemistry | LFP (Lithium Iron Phosphate) | LFP | NMC not accepted for utility-scale
Cell Supplier | Tier-1 (EVE, CATL, BYD, CALB, Hithium) | EVE 314Ah | Must be BNEF Tier 1
Round-Trip Efficiency | ≥86% (AC-AC full system) | ≥87% | Including auxiliary consumption
PCS Model | Kehua C-HUD series or equivalent | BCS1250K-C-HUD / BCS1000K-C-HUD | Grid-forming capable, ≥98% eff.
Grid-Forming Capability | Required — Virtual Synchronous Generator | Required | VSG mode, frequency/voltage support
Cycle Life | ≥6,000 at 90% DoD | ≥7,000 | To 70% SOH EOL
SOH Guarantee Year 5 | ≥85% | ≥85%
SOH Guarantee Year 10 | ≥79% | ≥80%
SOH Guarantee Year 15 | ≥70% | ≥70%
Operating Temperature | -10°C to +55°C | -20°C to +55°C | Cyprus ambient 0°C to 42°C
Container Rating | IP55 minimum | IP55 | Coastal environment
Production Lead Time | ≤90 days | 75 days | From advance payment
Shipping Time | ≤60 days | 45 days | China to Limassol CIF

## Pricing Curve
CIF PRICING CURVE — €/kWh vs System Size
Shows how CIF price decreases with system size. Based on actual portfolio data (Q1 2026) + target improvement.
CIF €/kWh by Total System MWh (All Durations)
System MWh | Actual CIF €/kWh (avg) | Target CIF €/kWh | Saving €/kWh | Saving % | Market Benchmark $/kWh | Notes
4 | 121.87 | 112 | 9.87 | 8.1% | ~$140 | Smallest system in portfolio
5 | 116.82 | 108 | 8.82 | 7.55% | ~$135 | 1-1.5 MW systems
8 | 104.22 | 96 | 8.22 | 7.89% | ~$125 | 2.5 MW systems
10 | 103 | 95 | 8 | 7.77% | ~$120 | 3-5 MW systems (avg)
15 | 103.84 | 95 | 8.84 | 8.51% | ~$115 | 4-5 MW systems
20 | 95 | 88 | 7 | 7.37% | ~$110 | 5-7 MW systems (avg)
25 | 99.5 | 92 | 7.5 | 7.54% | ~$108 | 7.5-8 MW systems
30 | 90.77 | 84 | 6.77 | 7.46% | ~$105 | 7 MW / 30 MWh
35 | 94.09 | 87 | 7.09 | 7.54% | ~$103 | 8 MW / 35 MWh
40 | 94.25 | 87 | 7.25 | 7.69% | ~$100 | 12 MW systems
60 | 82.03 | 76 | 6.03 | 7.35% | ~$95 | 8 MW / 60 MWh
100 | 87.54 | 80 | 7.54 | 8.61% | ~$90 | 25 MW / 100 MWh
200 | N/A | 74 | N/A | N/A | ~$82 | Target for future large projects
400 | N/A | 70 | N/A | N/A | ~$78 | Target for utility-scale 8h
Market benchmarks based on Ember (Oct 2025), BNEF, Saudi/Italy auction data. Converted at ~1.05 EUR/USD.
Current CIF scope includes PCS (Kehua C-HUD grid-forming), MV transformer, switchgear, BMS, EVE LFP cells, cooling, fire suppression — more scope than typical equipment-only benchmarks.