## Model A — 4h Hybrid
|  |  | Ref: LH-CY-PVBESS-APR2026 | April 2026 · Confidential
Cyprus PV + Battery Energy Storage — Model A: 4-Hour Hybrid Connection
PV day sales + BESS curtailment arbitrage · AE Solar Meteor TOPCon · Linyang LFP 4h
Metric | 1 MW + 4 MWh | 2.5 MW + 10 MWh | 5 MW + 20 MWh
CAPITAL EXPENDITURE
PV EPC — AE Solar Meteor TOPCon (€720/kWp) | 720000 | 1800000 | 3600000
BESS EPC — Linyang LFP 4h (all-in) | 600000 | 1250000 | 2400000
RTB licence acquisition (€380k/MW) | 380000 | 950000 | 1900000
EAC grid connection terms (€80k/MW) | 80000 | 200000 | 400000
MV cable to substation (1 km × €20k) | 20000 | 20000 | 20000
Permitting & documentation | 35000 | 35000 | 35000
Total CAPEX | 1835000 | 4255000 | 8355000
ANNUAL REVENUE (YEAR 1)
PV production (2,150 kWh/kWp) | 2,150 MWh | 5,375 MWh | 10,750 MWh
Direct PV sales (35% uncurtailed × €140.88/MWh) | 106012.2 | 265030.5 | 530061
BESS arbitrage (65% × 95% cap × RTE 86.32% × €182.99) | 209707.6196 | 524269.0491 | 1048538.0982
Less: aggregator fee (10%) | -31571.982 | -78929.9549 | -157859.9098
Net Annual Revenue | 284147.8377 | 710369.5942 | 1420739.1884
OPERATING COSTS & EBITDA
PV O&M (€15/kWp/yr) | -15000 | -37500 | -75000
BESS LTSA (€1,740/MWh/yr · 97% avail. · 15yr) | -6960 | -17400 | -34800
EBITDA | 262187.8377 | 655469.5942 | 1310939.1884
RETURN METRICS
Unlevered payback | 7.0 yr | 6.5 yr | 6.4 yr
Equity required (35%) | 642250 | 1489250 | 2924250
Senior debt (65% · 5.5% · 12yr) | 1192750 | 2765750 | 5430750
Annual debt service | -138393.8655 | -320907.8462 | -630125.7473
DSCR | 1.8945 | 2.0425 | 2.0804
Net cash to equity (post 15% CIT) | 118987.3763 | 316289.9858 | 641353.9249
Equity payback (levered) | 5.4 yr | 4.7 yr | 4.6 yr
KEY ASSUMPTIONS
PV EPC cost | €720/kWp all-in turnkey (AE Solar Meteor TOPCon bifacial)
PV specific yield | 2,150 kWh/kWp (25° south, white albedo 0.70, bifaciality 80%)
BESS RTE | 86.32% AC-AC round-trip efficiency (Linyang confirmed)
DAM evening peak | €182.99/MWh (TSOC sample Oct 2025–Feb 2026, 134 days)
DAM daytime average | €140.88/MWh (06:00–17:00 average)
Curtailment (Model A) | 65% (Agios Theodoros / Galascope validated model)
BESS capture rate (Model A) | 95% of curtailed energy captured
Aggregator fee | 10% of gross revenue
RTB acquisition | €380k/MW
EAC connection | €80k/MW (standard tier ≤8 MW)
MV cable | €20k/km · illustrative 1 km — site-specific
Finance | 65% LTV · 5.5% p.a. · 12yr annuity (factor 0.1160)
Depreciation | 20 years straight-line on total CAPEX
Cyprus CIT | 15% (from 1 Jan 2026, OECD Pillar II)
BESS LTSA | €1,740/MWh/yr · 97% availability · 15yr · Lighthief Cyprus
PV O&M | €15/kWp/yr · cleaning + inspection
Lighthief Cyprus Ltd · HE 477423 · +357 99 164 158 · alexander.papacosta@lighthief.com · lighthief.com · Strictly Confidential — April 2026

## Model B — 8h Flexible
|  |  | Ref: LH-CY-PVBESS-APR2026 | April 2026 · Confidential
Cyprus PV + Battery Energy Storage — Model B: 8-Hour Flexible Connection
100% nighttime BESS dispatch · zero daytime export · V4 internal costs × 1.40 · Linyang LFP 8h
Metric | 1 MW + 8 MWh | 2.5 MW + 20 MWh | 5 MW + 40 MWh
CAPITAL EXPENDITURE
PV EPC — AE Solar Meteor TOPCon (€720/kWp) | 720000 | 1800000 | 3600000
BESS EPC — Linyang LFP 8h (V4 internal × 1.40) | 1208000 | 2820000 | 5120000
RTB licence acquisition (€380k/MW) | 380000 | 950000 | 1900000
EAC grid connection terms (€80k/MW) | 80000 | 200000 | 400000
MV cable to substation (1 km × €20k) | 20000 | 20000 | 20000
Permitting & documentation | 35000 | 35000 | 35000
Total CAPEX | 2443000 | 5825000 | 11075000
ANNUAL REVENUE (YEAR 1)
PV production (2,150 kWh/kWp) | 2,150 MWh | 5,375 MWh | 10,750 MWh
BESS nighttime discharge (RTE 86.32%) | 1,856 MWh | 4,640 MWh | 9,279 MWh
Gross revenue (DAM evening peak × €182.99/MWh) | 339607.4812 | 849018.703 | 1698037.406
Less: aggregator fee (10%) | -33960.7481 | -84901.8703 | -169803.7406
Net Annual Revenue | 305646.7331 | 764116.8327 | 1528233.6654
OPERATING COSTS & EBITDA
PV O&M (€15/kWp/yr) | -15000 | -37500 | -75000
BESS LTSA (€1,740/MWh/yr · 97% avail. · 15yr) | -13920 | -34800 | -69600
EBITDA | 276726.7331 | 691816.8327 | 1383633.6654
RETURN METRICS
Unlevered payback | 8.8 yr | 8.4 yr | 8.0 yr
Equity required (35%) | 855050 | 2038750 | 3876250
Senior debt (65% · 5.5% · 12yr) | 1587950 | 3786250 | 7198750
Annual debt service | -184248.6177 | -439315.6766 | -835265.428
DSCR | 1.5019 | 1.5748 | 1.6565
Net cash to equity (post 15% CIT) | 92478.1154 | 252501.1561 | 548368.2374
Equity payback (levered) | 9.2 yr | 8.1 yr | 7.1 yr
KEY ASSUMPTIONS
PV EPC cost | €720/kWp all-in turnkey (AE Solar Meteor TOPCon bifacial)
PV specific yield | 2,150 kWh/kWp (25° south, white albedo 0.70, bifaciality 80%)
BESS RTE | 86.32% AC-AC round-trip efficiency (Linyang confirmed)
DAM evening peak | €182.99/MWh (TSOC sample Oct 2025–Feb 2026, 134 days)
DAM daytime average | N/A (100% BESS dispatch)
Curtailment (Model A) | N/A — 100% stored in BESS
BESS capture rate (Model A) | N/A
Aggregator fee | 10% of gross revenue
RTB acquisition | €380k/MW
EAC connection | €80k/MW (standard tier ≤8 MW)
MV cable | €20k/km · illustrative 1 km — site-specific
Finance | 65% LTV · 5.5% p.a. · 12yr annuity (factor 0.1160)
Depreciation | 20 years straight-line on total CAPEX
Cyprus CIT | 15% (from 1 Jan 2026, OECD Pillar II)
BESS LTSA | €1,740/MWh/yr · 97% availability · 15yr · Lighthief Cyprus
PV O&M | €15/kWp/yr · cleaning + inspection
Lighthief Cyprus Ltd · HE 477423 · +357 99 164 158 · alexander.papacosta@lighthief.com · lighthief.com · Strictly Confidential — April 2026